## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Lincoln
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2023-06-01
System Name: | Seal Rock Water District |  |  | ID#: 41 | 00798 |  | WTP : TP - | C
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 | OFF | 0.02 | 0.02 | 0.04 | 0.02 | OFF | 0.04
2 | OFF | OFF | 0.02 | 0.03 | 0.01 | 0.02 | 0.03
3 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
4 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
5 | 0.02 | 0.03 | 0.02 | 0.04 | 0.02 | 0.02 | 0.04
6 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | OFF | 0.02
7 | OFF | 0.04 | 0.04 | 0.02 | 0.01 | OFF | 0.04
8 | OFF | OFF | 0.07 | 0.02 | 0.01 | OFF | 0.07
9 | OFF | OFF | 0.01 | 0.02 | OFF | OFF | 0.02
10 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
11 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
12 | OFF | 0.04 | 0.02 | 0.04 | 0.02 | 0.03 | 0.04
13 | OFF | 0.02 | 0.02 | 0.03 | 0.02 | 0.02 | 0.03
14 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
15 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
16 | OFF | OFF | 0.02 | 0.02 | 0.04 | 0.02 | 0.04
17 | OFF | OFF | 0.02 | 0.01 | 0.01 | OFF | 0.02
18 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
19 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
20 | OFF | OFF | 0.03 | 0.02 | 0.02 | 0.02 | 0.02
21 | OFF | OFF | 0.01 | 0.02 | 0.02 | 0.02 | 0.02
22 | OFF | OFF | 0.02 | 0.04 | 0.03 | 0.04 | 0.04
23 | OFF | OFF | 0.02 | 0.03 | 0.02 | OFF | 0.03
24 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
25 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
26 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.03 | 0.03
27 | OFF | 0.03 | 0.02 | 0.02 | 0.02 | 0.03 | 0.03
28 | OFF | OFF | 0.02 | 0.02 | 0.03 | 0.02 | 0.03
29 | OFF | OFF | 0.03 | 0.02 | 0.03 | 0.02 | 0.03
30 | OFF | OFF | 0.04 | 0.04 | 0.04 | 0.02 | 0.04
31
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | YES | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | YES | YES |  | YES
Notes: |  |  |  |  | PRINTED NAME: Larry Estes
[5 empty] | Larry Estes |  |  | DATE: June 2023
[5 empty] | 541-961-7367 |  |  | T-09229
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | C
System Name: | SealRock Water District |  | ID#: 41 | 00798 | Month/Year: | 2023-06-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.62 | 40.58 | 25.1596 | 17.92 | 7.43 | 12.5825 | YES
2 | 0.74 | 53.96 | 39.9304 | 17.95 | 7.6 | 13.5626 | YES
3 | 0.71 | 38.89 | 27.6119 | 18.2 | 7.8 | 14.3175 | YES
4
5 | 0.78 | 35.51 | 27.6978 | 17.58 | 7.71 | 14.5487 | YES
6 | 0.73 | 20.37 | 14.8701 | 18.42 | 7.76 | 13.9321 | YES
7 | 0.82 | 41.03 | 33.6446 | 18.54 | 7.75 | 13.9117 | YES
8 | 0.81 | 57.88 | 46.8828 | 19 | 7.71 | 13.2755 | YES
9 | 0.88 | 71.77 | 63.1576 | 18.93 | 7.58 | 12.81 | YES
10 | 0.78 | 20.57 | 16.0446 | 18.7 | 7.62 | 13.054 | YES
11
12 | 0.79 | 42.34 | 33.4486 | 18.27 | 7.42 | 12.4855 | YES
13 | 0.84 | 54.67 | 45.9228 | 20.33 | 7.51 | 11.307 | YES
14 | 1.59 | 40.69 | 64.6971 | 19.82 | 7.6 | 13.1878 | YES
15 | 1.58 | 41.72 | 65.9176 | 19.84 | 7.66 | 13.452 | YES | 1
16 | 1.46 | 40.05 | 58.473 | 19.29 | 7.61 | 13.5128 | YES
17 | 1.49 | 42.08 | 62.6992 | 20.47 | 7.54 | 12.2052 | YES
18
19 | 1.71 | 40.04 | 68.4684 | 21.71 | 7.56 | 11.6026 | YES
20 | 1.76 | 31.83 | 56.0208 | 19.4 | 7.71 | 14.407 | YES
21 | 1.64 | 42.36 | 69.4704 | 19.78 | 7.82 | 14.432 | YES
22 | 1.66 | 44.96 | 74.6336 | 19.78 | 7.77 | 14.199 | YES
23 | 1.64 | 45.49 | 74.6036 | 20.35 | 7.83 | 13.944 | YES
24 | 1.01 | 68.07 | 68.7507 | 20.31 | 7.68 | 12.3022 | YES
25
26 | 1.86 | 41.42 | 77.0412 | 20.19 | 7.48 | 12.6887 | YES
27 | 1.78 | 35.73 | 63.5994 | 21.26 | 7.68 | 12.6073 | YES
28 | 1.51 | 34.48 | 52.0648 | 21.29 | 7.55 | 11.6205 | YES
29 | 1.48 | 34.35 | 50.838 | 22.02 | 7.71 | 11.7047 | YES
30 | 1.39 | 35.95 | 49.9705 | 22.18 | 7.66 | 11.2479 | YES
31
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2