## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Lincoln
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2023-07-01
System Name: | Seal Rock Water District |  |  | ID#: 41 | 00798 |  | WTP : TP - | C
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
2 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
3 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
4 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.01 | 0.02
5 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
6 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
7 | OFF | OFF | 0.01 | 0.01 | 0.03 | 0.02 | 0.03
8 | OFF | OFF | OFF | OFF | OFF | 0.02 | 0.02
9 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
10 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | OFF
11 | OFF | 0.03 | 0.02 | 0.01 | 0.03 | 0.03 | 0.03
12 | 0.04 | 0.04 | 0.02 | 0.03 | 0.02 | 0.03 | 0.04
13 | OFF | OFF | 0.05 | 0.02 | 0.03 | 0.03 | 0.05
14 | 0.03 | 0.03 | 0.02 | 0.03 | 0.02 | 0.02 | 0.03
15 | OFF | OFF | 0.04 | 0.03 | 0.03 | OFF | 0.04
16 | OFF | 0.06 | 0.06 | 0.07 | 0.07 | 0.05 | 0.07
17 | 0.09 | 0.09 | 0.09 | 0.05 | 0.05 | 0.02 | 0.09
18 | 0.02 | 0.02 | 0.02 | 0.03 | 0.03 | 0.02 | 0.03
19 | 0.02 | 0.02 | 0.05 | 0.02 | 0.03 | 0.04 | 0.05
20 | OFF | OFF | 0.02 | 0.03 | 0.03 | 0.03 | 0.03
21 | OFF | OFF | 0.02 | 0.03 | 0.02 | 0.02 | 0.03
22 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
23 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
24 | OFF | 0.02 | 0.04 | 0.03 | 0.04 | 0.01 | 0.04
25 | 0.02 | 0.01 | 0.01 | 0.02 | 0.03 | 0.01 | 0.03
26 | 0.01 | 0.02 | 0.03 | 0.07 | 0.01 | 0.01 | 0.07
27 | 0.02 | 0.02 | 0.01 | 0.07 | 0.01 | 0.01 | 0.07
28 | 0.01 | OFF | 0.01 | 0.06 | 0.01 | 0.06 | 0.06
29 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
30 | OFF | OFF | OFF | 0.01 | 0.01 | 0.03 | OFF
31 | 0.03 | 0.03 | 0.03 | 0.04 | 0.03 | 0.01 | 0.04
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | YES | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | YES | YES |  | YES
Notes: |  |  |  |  | PRINTED NAME: Larry Estes
[5 empty] | Larry Estes |  |  | DATE:Aug 2 2023
[5 empty] | 541-961-7367 |  |  | CERT #: T-09229
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | C
System Name: | Seal Rock Water District |  | ID#: 41 | 00798 | Month/Year: | 2023-07-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.13 | 108.84 | 122.9892 | 22.13 | 7.51 | 10.3544 | YES
2 | 1.06 | 24.81 | 26.2986 | 22.24 | 7.49 | 10.1187 | YES
3 | 1.5 | 36.07 | 54.105 | 21.18 | 7.46 | 11.3065 | YES
4 | 1.06 | 26.28 | 27.8568 | 22.2 | 7.56 | 10.4162 | YES
5 | 1.09 | 21.44 | 23.3696 | 21.8 | 7.06 | 8.8976 | YES
6 | 1.5 | 41.85 | 62.775 | 21.98 | 7.08 | 9.2873 | YES
7 | 1.37 | 33.35 | 45.6895 | 21.2 | 7.15 | 9.9027 | YES
8 | 1.17 | 29.27 | 34.2459 | 21.18 | 7.17 | 9.7626 | YES
9 | 1.12 | 20.86 | 23.3632 | 21.54 | 7.34 | 10.0978 | YES
10 | 1.15 | 35.87 | 41.2505 | 22.2 | 7.21 | 9.2272 | YES
11 | 1.23 | 32.51 | 39.9873 | 22.4 | 7.75 | 11.253 | YES
12 | 0.85 | 30.84 | 26.214 | 22.2 | 7.59 | 10.282 | YES
13 | 0.91 | 20.86 | 18.9826 | 23.31 | 7.24 | 8.4159 | YES
14 | 0.86 | 29.37 | 25.2582 | 23.3 | 7.5 | 9.2368 | YES
15 | 1.05 | 21.18 | 22.239 | 23.76 | 7.08 | 7.8072 | YES
16 | 1.31 | 33.86 | 44.3566 | 23.57 | 7.18 | 8.4676 | YES
17 | 1.27 | 52.63 | 66.8401 | 24.05 | 7 | 7.618 | YES
18 | 1.21 | 40.82 | 49.3922 | 24.02 | 7.14 | 7.9944 | YES
19 | 1.25 | 46.03 | 57.5375 | 23.53 | 7.08 | 8.1182 | YES
20 | 1.15 | 47.09 | 54.1535 | 22.63 | 7.02 | 8.3405 | YES
21 | 1.14 | 51.72 | 58.9608 | 22.54 | 7.05 | 8.4778 | YES
22
23 | 0.88 | 37.37 | 32.8856 | 22.52 | 7.14 | 8.5217 | YES
24 | 0.91 | 76.33 | 69.4603 | 23.31 | 7.16 | 8.1647 | YES
25 | 0.82 | 34.75 | 28.495 | 23.47 | 7.19 | 8.0831 | YES
26 | 1.28 | 38.07 | 48.7296 | 23.3 | 7.34 | 9.13 | YES
27 | 1.16 | 52.69 | 61.1204 | 23.65 | 7.29 | 8.6275 | YES
28 | 1.18 | 68.88 | 81.2784 | 23.65 | 7.18 | 8.295 | YES
29 | 0.99 | 25.03 | 24.7797 | 23.52 | 7 | 7.6451 | YES
30 | 1.03 | 77.62 | 79.9486 | 23.8 | 7.14 | 7.9468 | YES
31 | 1.2 | 78.53 | 94.236 | 24.24 | 7.1 | 7.7473 | YES
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2