## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Lincoln
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2023-09-23
System Name: | Seal Rock Water District |  |  | ID#: 41 | 00798 |  | WTP : TP - | C
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 | OFF | OFF | 0.01 | 0.03 | OFF | OFF | 0.03
2 | OFF | OFF | OFF | OFF | OFF | 0.04 | 0.04
3 | 0.04 | 0.04 | OFF | OFF | OFF | 0.04 | 0.04
4 | 0.04 | OFF | OFF | OFF | 0.01 | 0.05 | 0.05
5 | 0.04 | OFF | OFF | 0.03 | 0.04 | 0.04 | 0.04
6 | OFF | OFF | 0.04 | 0.04 | 0.03 | 0.04 | 0.04
7 | 0.03 | 0.03 | 0.05 | 0.04 | 0.04 | 0.04 | 0.05
8 | OFF | 0.04 | OFF | OFF | 0.05 | 0.04 | 0.05
9 | 0.04 | OFF | OFF | OFF | OFF | 0.05 | 0.05
10 | 0.03 | 0.04 | 0.02 | OFF | OFF | OFF | 0.04
11 | 0.04 | 0.04 | 0.03 | 0.03 | OFF | OFF | 0.04
12 | OFF | OFF | 0.01 | 0.02 | 0.01 | 0.01 | 0.02
13 | OFF | OFF | OFF | 0.02 | 0.03 | 0.01 | 0.03
14 | OFF | OFF | OFF | 0.01 | 0.04 | OFF | 0.04
15 | 0.02 | 0.01 | 0.01 | 0.03 | 0.03 | OFF | 0.03
16 | OFF | OFF | 0.01 | 0.04 | 0.01 | OFF | 0.04
17 | OFF | OFF | OFF | 0.01 | 0.01 | 0.02 | 0.02
18 | 0.01 | 0.01 | OFF | OFF | OFF | OFF | 0.01
19 | OFF | OFF | OFF | 0.04 | 0.01 | 0.01 | 0.04
20 | 0.02 | 0.01 | 0.03 | 0.01 | 0.02 | OFF | 0.03
21 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
22 | OFF | OFF | 0.02 | 0.02 | 0.01 | OFF | 0.02
23 | 0.03 | 0.01 | OFF | OFF | 0.02 | 0.01 | 0.03
24 | 0.03 | 0.02 | OFF | OFF | OFF | OFF | 0.03
25 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
26 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
27 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
28 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
29 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
30 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
31
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | YES | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | YES | YES |  | YES
Notes: 9/25-9/30 WTP shut down due to salinity and routine maintenance. We have brought on our secondary source of water as of 9/25/2023 through the end of the month. |  |  |  |  | PRINTED NAME: Larry Estes
[5 empty] | Larry Estes |  |  | DATE:10-2-2023
[5 empty] | 541-562-7715 |  |  | CERT #:T-09229
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | C
System Name: | SealRock Water District |  | ID#: 41 | 00798 | Month/Year: | Sept. 2023 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.16 | 82.52 | 95.7232 | 22.2 | 7.2 | 9.2032 | YES
2 | 1.07 | 45.38 | 48.5566 | 22.14 | 6.7 | 7.5672 | YES
3 | 1.02 | 28.92 | 29.4984 | 22.8 | 6.8 | 7.4693 | YES
4 | 1.02 | 38.31 | 39.0762 | 22.9 | 6.9 | 7.7059 | YES
5 | 1.22 | 76.72 | 93.5984 | 22.9 | 6.9 | 7.8881 | YES
6 | 1.13 | 58.09 | 65.6417 | 22.2 | 6.85 | 8.0342 | YES
7 | 1.58 | 108.14 | 170.8612 | 22.04 | 7.13 | 9.5132 | YES
8 | 1.03 | 69.01 | 71.0803 | 22.1 | 7.05 | 8.6246 | YES
9 | 1.02 | 56.02 | 57.1404 | 21.89 | 7.3 | 9.6025 | YES
10 | 1.05 | 57.97 | 60.8685 | 21.95 | 7.23 | 9.3471 | YES
11 | 1.03 | 66.12 | 68.1036 | 21.9 | 7.25 | 9.428 | YES
12 | 1.02 | 44.1 | 44.982 | 21.4 | 6.97 | 8.7658 | YES
13 | 1.08 | 54.82 | 59.2056 | 21.5 | 6.93 | 8.6357 | YES
14 | 1.02 | 57.45 | 58.599 | 21.66 | 6.91 | 8.4188 | YES
15 | 1.06 | 68.11 | 72.1966 | 21.4 | 6.92 | 8.6418 | YES
16 | 0.95 | 54.26 | 51.547 | 21.6 | 6.8 | 8.0424 | YES
17 | 0.96 | 60.55 | 58.128 | 20.98 | 6.83 | 8.4956 | YES
18 | 1.1 | 61.37 | 67.507 | 20.6 | 6.87 | 8.996 | YES
19 | 0.94 | 61.23 | 57.5562 | 20.28 | 6.84 | 8.923 | YES
20 | 1 | 67.39 | 67.39 | 19.95 | 6.82 | 9.12 | YES
21
22 | 1.02 | 32.64 | 33.2928 | 18.7 | 6.88 | 10.1762 | YES
23 | 0.93 | 62.95 | 58.5435 | 18.9 | 6.92 | 10.0861 | YES
24 | 0.87 | 67.85 | 59.0295 | 18.7 | 6.91 | 10.1148 | YES
25
26
27
28
29
30
31
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2