## pg 1
Membrane Filter Monthly Operating Report |  |  |  |  | County: | Lincoln
| System Name: | Seal Rock Water District |  |  | Month/Year: | Nov. 2023
| PWS ID#: 41 - | 00798 |  |  | Minimum test pressure applied ¦¦ req'd: | 19.0________ psi ¦¦ _19.5_______ psi
| Plant ID: WTP - | C | (e.g., "A")
[6 empty] | DIT = Direct Integrity Test on filter(s) [Yes, No, or "off" if all filters are offline] a | DIT Daily
|  |  | PDR = Pressure Decay Rate | PDRMax [psi/min] | LRC [log removal]
|  |  | LRC = Log Removal Credit |  | 4
Day | CFE Daily Turbidity [NTU] | Highest CFE♣ [NTU] | Highest IFE [NTU] (>15 min duration) | Highest PDR of day [psi/min] | Lowest LRVambient of day [log removal] |  | [Y/N] or "off"
1 | OFF | OFF | OFF | OFF | OFF |  | OFF
2 | OFF | OFF | OFF | OFF | OFF |  | OFF
3 | OFF | OFF | OFF | OFF | OFF |  | OFF
4 | OFF | OFF | OFF | OFF | OFF |  | OFF
5 | OFF | OFF | OFF | OFF | OFF |  | OFF
6 | OFF | OFF | OFF | OFF | OFF |  | OFF
7 | 0.03 | 0.03 | 0.03 | 0.05 | 4.39 |  | Yes
8 | 0.04 | 0.04 | 0.04 | 0.04 | 4.44 |  | Yes
9 | 0.03 | 0.03 | 0.03 | 0.04 | 4.45 |  | Yes
10 | 0.03 | 0.03 | 0.03 | 0.04 | 4.41 |  | Yes
11 | OFF | OFF | OFF | OFF | OFF |  | OFF
12 | OFF | OFF | OFF | OFF | OFF |  | OFF
13 | 0.03 | 0.03 | 0.03 | 0.03 | 4.37 |  | Yes
14 | 0.03 | 0.03 | 0.03 | 0.03 | 4.45 |  | Yes
15 | 0.03 | 0.03 | 0.03 | 0.03 | 4.25 |  | Yes
16 | 0.03 | 0.03 | 0.03 | 0.04 | 4.25 |  | Yes
17 | 0.03 | 0.03 | 0.03 | 0.05 | 4.25 |  | Yes
18 | OFF | OFF | OFF | OFF | OFF |  | OFF
19 | OFF | OFF | OFF | OFF | OFF |  | OFF
20 | 0.03 | 0.03 | 0.03 | 0.06 | 4.26 |  | Yes
21 | 0.02 | 0.02 | 0.02 | 0.04 | 4.31 |  | Yes
22 | 0.03 | 0.03 | 0.03 | 0.04 | 4.28 |  | Yes
23 | 0.03 | 0.03 | 0.03 | 0.04 | 4.24 |  | Yes
24 | OFF | OFF | OFF | OFF | OFF |  | OFF
25 | OFF | OFF | OFF | OFF | OFF |  | OFF
26 | 0.03 | 0.03 | 0.03 | 0.03 | 4.24 |  | Yes
27 | OFF | OFF | OFF | OFF | OFF |  | OFF
28 | OFF | OFF | OFF | OFF | OFF |  | OFF
29 | OFF | OFF | OFF | OFF | OFF |  | OFF
30 | OFF | OFF | OFF | OFF | OFF |  | OFF
31
Compliance summary (operator to complete any blank fields)
95% of daily turbidity readings ≤ 1 NTU? [YES] |  | All turbidity readings ≤ 5 NTU? [YES] |  | All IFE turbidity readings ≤ 0.15 NTU? [YES] |  | Performance std met? [YES] (PDR ≤ PDRMax, LRV ≥ ) | DIT Daily?
Yes |  | Yes |  | Yes |  | Yes | Yes
CT's met daily? (p. 2) |  | All Cl2 residual at EP ≥ 0.2 mg/L? |  | PDR < PDRMax? |  | LRVambient > LRC?
Yes |  | Yes |  | Yes |  | Yes
PRINTED NAME: |  | Larry Estes |  |  | DATE: | 2023-12-05
SIGNATURE: |  | Larry Estes |  |  | WT CERT #: | T-09229
Notes:Nov 1-6 2023 on Newport water Secondary source |  |  |  |  | PHONE #: | 541-961-7367
11-27-30 on Newport secondary | [6 empty] | p. 1 of 2

## pg 2
Disinfection Monthly Operating Report
| System Name: | Seal Rock Water District
| PWS ID#: 41 - | 00798 | [5 empty] | 0.5 | b Log Inactivation
| Plant ID : WTP - | C | [6 empty] | Required via Disinfection
Day | Minimum Cl2 Residual at 1st User ( C ) ♦ [mg/L = ppm] | Contact Time (T) [minutes] | Actual CT C x T (Formula) | Temp [° C] | pH | Required CT (Formula) | CT Met? ♦ [Yes / No] (Formula) | Peak Hourly Demand Flow [GPM] | Notes (e.g. "Plant Off")
1 | [8 empty] | OFF
2 | [8 empty] | OFF
3 | [8 empty] | OFF
4 | [8 empty] | OFF
5 | [8 empty] | OFF
6 | [8 empty] | OFF
7 | 1.54 | 31.36 | 48.2944 | 15.2 | 7.23 | 15.5656 | YES | 800
8 | 1.81 | 71.7 | 129.777 | 15 | 7.32 | 16.8176 | YES | 787
9 | 1.1 | 54.61 | 60.071 | 14.7 | 7.27 | 15.5353 | YES | 677
10 | 1.46 | 57.69 | 84.2274 | 14.8 | 7.34 | 16.4997 | YES | 684
11 | 1.32 | 39.22 | 51.7704 | 14.6 | 7.71 | 18.8668 | YES | 865
12 | [8 empty] | OFF
13 | 1.29 | 45.45 | 58.6305 | 14.8 | 7.58 | 17.6853 | YES | 697
14 | 1.22 | 59.41 | 72.4802 | 14.95 | 7.41 | 16.3127 | YES | 707
15 | 2.8 | 76.48 | 214.144 | 14.59 | 7.43 | 20.1377 | YES | 787
16 | 2.32 | 61.95 | 143.724 | 14.2 | 7.11 | 17.392 | YES | 792
17 | 2.03 | 75.78 | 153.8334 | 13.1 | 7.14 | 18.3073 | YES | 671
18 | 1.67 | 58.12 | 97.0604 | 13.2 | 7.21 | 17.9149 | YES | 658
19 | [8 empty] | OFF
20 | 1.46 | 87.33 | 127.5018 | 12.02 | 7.1 | 18.4409 | YES | 549
21 | 1.41 | 53.54 | 75.4914 | 11.9 | 7.09 | 18.4184 | YES | 581
22 | 1.63 | 45.08 | 73.4804 | 12.6 | 7.4 | 19.9058 | YES | 883
23 | 1.59 | 66.79 | 106.1961 | 12.3 | 7.7 | 22.6455 | YES | 624
24 | 1.43 | 33.75 | 48.2625 | 13.8 | 7.8 | 20.8238 | YES | 686
25 | [8 empty] | OFF
26 | 1.61 | 33.43 | 53.8223 | 13.5 | 7.9 | 22.4907 | YES | 699
27 | [8 empty] | OFF
28 | [8 empty] | OFF
29 | [8 empty] | OFF
30 | [8 empty] | OFF
31
♦ If chlorine concentration at entry point < 0.2 mg/L, or CT not met, notify DWS within 24 hours.
Submit this monthly report by the 10th of following month by
| mail: | Drinking Water Services
PO Box 14350
Portland, OR 97293-0350
| email: | dwp.dmce@odhsoha.oregon.gov
| fax: | 971-673-0458 | [7 empty] | p. 2 of 2

## Additional Info
Definitions & Additional Information
Glossary of Terms:
CFE = Combined Filter Effluent IFE = Individual Filter Effluent
PDR = Pressure Decay Rate @ DIT = Direct Integrity Test LRC = Log Removal Credit
LRV = Log Removal Value TMP = Transmembrane Pressure
Cl2 = Chlorine CT = chlorine Concentration x contact Time
LRVambient: The preferred performance metric Oregon is moving towards
LRVambient is a performance metric of the filter's Cryptosporidium removal efficiency; [log] units.
LRVambient is calculated using the last DIT results & operating condtions (e.g., flow, temp. & TMP)
A filter whose LRVambient is less than the LRC must be taken off-line, repaired and then re-tested.
LRVambient is an LRV calculated using most recent DIT results (e.g., PDR in psi/min), current filter
flowrate, water temperature, and TMP.
An LRVambient of 4-log is equivalent to 99.99% removal of Cryptosporidium.
The nature of membrane filtration requires higher pathogen removal rates. Therefore, 4-log is
typically the minimum pathogen removal target.
Highest PDR (Pressure Decay Rate):
Enter the highest pressure decay rate in psi/min measured for DITs of all operating filters in a day.
A filter whose PDR exceeds the PDRMax must be taken off-line, repaired and re-tested.
(PDRMax is an Upper Control Limit (UCL) based on the DIT Pressure Decay Rate)
DIT Daily:
Enter "Y" if ALL filters operating in a given day were subjected to a DIT.
Enter "N" if ANY operating filter did not have a DIT.
Enter "Off" if ALL filters were off-line for the day.
Each filter producing water for human consumption in a given day must undergo a DIT
Highest IFE [NTU]: Must be continuously monitored.
If ever exceeds 0.15 NTU for > 15 minutes: Run a DIT, & complete Turbidity Triggered DIT form
Highest CFE [NTU]:
Data is collected for optimization purposes. Not for compliance.
Revised 7/31/2023

## NTU Triggered DIT
Turbidity-Triggered Direct Integrity Test (DIT) Reporting Form | [5 empty] | OHA - Drinking Water Services
To be used when IFE exceeds 0.15 NTU, and submitted to OHA-DWS ♠
Water System Name: | Seal Rock Water District
Water System ID: | 00798 | 00798 Water System Profile on DataOnline
Treatment Plant ID: WTP- | C | PDRMax = | maximum allowed pressure decay rate for a passing DIT
County: | Lincoln | LRC = | Log Removal Credit granted for filtration, LRVambient must be > LRC.
Month - Year: | Nov. 2023
Date/Time and membrane unit(s) affected |  |  | Pressure Decay Rate (PDR) [psi/min]: | 0 | LRC: | 4
Date/Time | Membrane unit/skid/cell ID# | Turbidity level > 0.15 NTU resulting in DIT [NTU] | Corrective action | DIT Re-test Results [psi/min] | Return-to-service turbidity [NTU] | Return-to-service LRVambient [log]
Monthly Summary
All return to service turbidity readings ≤ 0.15 NTU? (Enter Yes or No) a
All membrane units removed from service until a DIT passes? (Enter Yes or No) a
All return to service LRVambient > LRC? (Enter Yes or No) a
Name:
Signature: |  |  | Date:
Phone #: |  |  | WT Cert #:
♠ OAR 333-061-0036(5)(d)(C)(iv) states that if indirect integrity monitoring includes turbidity and the filtrate turbidity readings are above 0.15 NTU for a period greater than 15 minutes (i.e., two consecutive 15-minute readings above 0.15 NTU), direct integrity testing in accordance with subparagraphs (5)(d)(B)(i) through (v) of this rule must immediately be performed on the associated membrane unit.
Return by 10th of following month by email, fax, or mail to:
dwp.dmce@odhsoha.oregon.gov; 971-673-0458; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350 | [5 empty] | Revised 2/17/2023