## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Lincoln
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2021-06-01
System Name: | Siletz |  |  | ID#: 41 00821 |  |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | PLANT | OFF | 0.02 | 0.02 | PLANT | OFF | 0.02
2 | PLANT | OFF | 0.02 | 0.02 | PLANT | OFF | 0.02
3 | PLANT | OFF | 0.02 | 0.02 | PLANT | OFF | 0.02
4 | PLANT | OFF | 0.02 | 0.02 | PLANT | OFF | 0.02
5 | PLANT | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
6 | PLANT | OFF | 0.02 | 0.02 | PLANT | OFF | 0.02
7 | PLANT | OFF | 0.02 | 0.02 | PLANT | OFF | 0.02
8 | PLANT | OFF | 0.02 | 0.02 | PLANT | OFF | 0.02
9 | PLANT | OFF | 0.02 | 0.02 | PLANT | OFF | 0.02
10 | PLANT | OFF | 0.02 | 0.02 | PLANT | OFF | 0.02
11 | PLANT | OFF | 0.02 | 0.02 | PLANT | OFF | 0.02
12 | PLANT | OFF | 0.02 | 0.02 | PLANT | OFF | 0.02
13 | PLANT | OFF | 0.02 | 0.02 | PLANT | OFF | 0.02
14 | PLANT | OFF | 0.02 | 0.02 | PLANT | OFF | 0.02
15 | PLANT | OFF | 0.02 | 0.02 | PLANT | OFF | 0.02
16 | PLANT | OFF | 0.02 | 0.02 | PLANT | OFF | 0.02
17 | PLANT | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
18 | PLANT | OFF | 0.02 | 0.02 | PLANT | OFF | 0.02
19 | PLANT | OFF | 0.02 | 0.02 | PLANT | OFF | 0.02
20 | PLANT | OFF | 0.02 | 0.02 | PLANT | OFF | 0.02
21 | PLANT | OFF
22 | PLANT | OFF
23 | PLANT | OFF
24 | PLANT | OFF
25 | PLANT | OFF
26 | PLANT | OFF
27 | PLANT | OFF
28 | PLANT | OFF
29 | PLANT | OFF
30 | PLANT | OFF
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
All turbidity readings < IFE2 triggers |  |  |  | Yes / No
Notes: |  |  |  |  | NAME: Allen Middaugh
[5 empty] | SIGNATURE: |  |  | Date:
[5 empty] | PHONE #: (541) 444-2521 |  |  | CERT #: 5265
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - :
System Name: | Siletz |  | ID#: 41 00821 |  | Month/Year: | 2021-06-01 | Disinfection Giardia Log Inactive: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.9 | 179 | 161.1 | 17.8 | 7.11 | 11.6241 | YES | 350
2 | 0.9 | 179 | 161.1 | 17.5 | 7.11 | 11.861 | YES | 350
3 | 0.9 | 179 | 161.1 | 17.7 | 7.1 | 11.6589 | YES | 350
4 | 0.9 | 179 | 161.1 | 18 | 7.07 | 11.2984 | YES | 350
5 | 1 | 179 | 179 | 17.9 | 7.07 | 11.5063 | YES | 350
6 | 0.9 | 179 | 161.1 | 17.4 | 7.05 | 11.6764 | YES | 350
7 | 0.9 | 179 | 161.1 | 17.5 | 7.07 | 11.6851 | YES | 350
8 | 0.9 | 179 | 161.1 | 17.4 | 7.1 | 11.8965 | YES | 350
9 | 0.9 | 179 | 161.1 | 17.6 | 7.16 | 12.0035 | YES | 350
10 | 0.9 | 179 | 161.1 | 17.9 | 7.29 | 12.3487 | YES | 350
11 | 0.9 | 179 | 161.1 | 17.9 | 7.12 | 11.5894 | YES | 350
12 | 0.9 | 179 | 161.1 | 17.7 | 7.26 | 12.3764 | YES | 350
13 | 0.9 | 179 | 161.1 | 17.9 | 7.13 | 11.6327 | YES | 350
14 | 0.9 | 179 | 161.1 | 17.9 | 7.06 | 11.3323 | YES | 350
15 | 0.9 | 179 | 161.1 | 17.8 | 7.12 | 11.6676 | YES | 350
16 | 0.9 | 179 | 161.1 | 17.9 | 7.14 | 11.6763 | YES | 350
17 | 1 | 179 | 179 | 18 | 7.1 | 11.558 | YES | 350
18 | 1 | 179 | 179 | 18.1 | 7.12 | 11.5666 | YES | 350
19 | 1 | 179 | 179 | 18.2 | 7.14 | 11.5752 | YES | 350
20 | 1 | 179 | 179 | 18 | 7.13 | 11.6883 | YES | 350
21 | 1 | 179 | 179 | 18.6 | 7.05 | 10.8944 | YES | 350
22 | 0.9 | 179 | 161.1 | 18.6 | 7.11 | 11.0144 | YES | 350
23 | 0.9 | 179 | 161.1 | 18.4 | 7.06 | 10.9569 | YES | 350
24 | 0.9 | 179 | 161.1 | 18.4 | 7.11 | 11.1639 | YES | 350
25 |  | 179 | [5 empty] | 350
26 |  | 179 | [5 empty] | 350
27 |  | 179 | [5 empty] | 350
28 |  | 179 | [5 empty] | 350
29 |  | 179 | [5 empty] | 350
30 |  | 179 | [5 empty] | 350
31 |  | 179 | [5 empty] | 350
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2