## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Lincoln
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2023-04-01
System Name: | Siletz |  |  | ID#: 41 00821 |  |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | Off | Off | 0.02 | 0.02 | Off | Off | 0.02
2 | Off | Off | 0.02 | 0.02 | Off | Off | 0.02
3 | Off | Off | 0.02 | 0.02 | Off | Off | 0.02
4 | Off | Off | 0.02 | 0.02 | Off | Off | 0.02
5 | Off | Off | 0.02 | 0.02 | Off | Off | 0.02
6 | Off | Off | 0.02 | 0.02 | Off | Off | 0.02
7 | Off | Off | 0.02 | 0.02 | Off | Off | 0.02
8 | Off | Off | 0.02 | 0.02 | Off | Off | 0.02
9 | Off | Off | 0.02 | 0.02 | Off | Off | 0.02
10 | Off | Off | 0.02 | 0.02 | Off | Off | 0.02
11 | Off | Off | 0.02 | 0.02 | Off | Off | 0.02
12 | Off | Off | 0.02 | 0.02 | Off | Off | 0.02
13 | Off | Off | 0.02 | 0.02 | Off | Off | 0.02
14 | Off | Off | 0.02 | 0.02 | Off | Off | 0.02
15 | Off | Off | 0.02 | 0.02 | Off | Off | 0.02
16 | Off | Off | 0.02 | 0.02 | Off | Off | 0.02
17 | Off | Off | 0.02 | 0.02 | Off | Off | 0.02
18 | Off | Off | 0.02 | 0.02 | Off | Off | 0.02
19 | Off | Off | 0.02 | 0.02 | Off | Off | 0.02
20 | Off | Off | 0.02 | 0.02 | Off | Off | 0.02
21 | Off | Off | 0.02 | 0.02 | Off | Off | 0.02
22 | Off | Off | 0.02 | 0.02 | Off | Off | 0.02
23 | Off | Off | 0.02 | 0.02 | Off | Off | 0.02
24 | Off | Off | 0.02 | 0.02 | Off | Off | 0.02
25 | Off | Off | 0.02 | 0.02 | Off | Off | 0.02
26 | Off | Off | 0.02 | 0.02 | Off | Off | 0.02
27 | Off | Off | 0.02 | 0.02 | Off | Off | 0.02
28 | Off | Off | 0.02 | 0.02 | Off | Off | 0.02
29 | Off | Off | 0.02 | 0.02 | Off | Off | 0.02
30 | Off | Off | 0.02 | 0.02 | Off | Off | 0.02
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Allen Middaugh
[5 empty] | SIGNATURE: |  |  | 2023-05-01
[5 empty] | PHONE #: ( 541 ) 444-2521 |  |  | CERT #: 5265
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - :
System Name: | Siletz |  | ID#: 41 00821 |  | Month/Year: | 2023-04-01 | Disinfection Giardia Log Inactive: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.99 | 179 | 177.21 | 8.7 | 7.28 | 23.153 | YES | 350
2 | 1 | 179 | 179 | 9.3 | 7.28 | 22.2767 | YES | 350
3 | 1 | 179 | 179 | 8.8 | 7.24 | 22.7033 | YES | 350
4 | 0.98 | 179 | 175.42 | 8.9 | 7.29 | 22.9029 | YES | 350
5 | 0.97 | 179 | 173.63 | 9.2 | 7.27 | 22.2699 | YES | 350
6 | 1.02 | 179 | 182.58 | 9.5 | 7.24 | 21.7268 | YES | 350
7 | 0.97 | 179 | 173.63 | 9.5 | 7.25 | 21.6806 | YES | 350
8 | 0.95 | 179 | 170.05 | 9.4 | 7.25 | 21.7747 | YES | 350
9 | 0.97 | 179 | 173.63 | 9.9 | 7.27 | 21.2661 | YES | 350
10 | 0.97 | 179 | 173.63 | 10 | 7.26 | 21.053 | YES | 350
11 | 0.94 | 179 | 168.26 | 9.5 | 7.26 | 21.6833 | YES | 350
12 | 0.96 | 179 | 171.84 | 9.8 | 7.26 | 21.3075 | YES | 350
13 | 0.96 | 179 | 171.84 | 9.6 | 7.26 | 21.5897 | YES | 350
14 | 0.99 | 179 | 177.2 | 9.6 | 7.26 | 21.6628 | YES | 350
15 | 0.93 | 179 | 166.47 | 10.6 | 7.25 | 20.0812 | YES | 350
16 | 0.97 | 179 | 173.63 | 10.9 | 7.17 | 19.239 | YES | 350
17 | 0.93 | 179 | 166.47 | 10.1 | 7.31 | 21.1889 | YES | 350
18 | 0.89 | 179 | 159.31 | 10.3 | 7.29 | 20.6738 | YES | 350
19 | 0.96 | 179 | 171.84 | 9.7 | 7.24 | 21.2982 | YES | 350
20 | 0.93 | 179 | 166.47 | 9.4 | 7.28 | 21.9558 | YES | 350
21 | 0.94 | 179 | 168.26 | 9.9 | 7.25 | 21.0466 | YES | 350
22 | 0.94 | 179 | 168.26 | 11 | 7.26 | 19.6542 | YES | 350
23 | 0.9 | 179 | 161.1 | 11.7 | 7.2 | 18.3151 | YES | 350
24 | 0.93 | 179 | 166.47 | 10.2 | 7.27 | 20.7579 | YES | 350
25 | 0.93 | 179 | 166.47 | 10.1 | 7.27 | 20.8944 | YES | 350
26 | 0.92 | 179 | 164.68 | 10.9 | 7.25 | 19.6701 | YES | 350
27 | 0.93 | 179 | 166.47 | 10.8 | 7.25 | 19.8208 | YES | 350
28 | 0.9 | 179 | 161.1 | 11.4 | 7.24 | 18.9333 | YES | 350
29 | 0.93 | 179 | 166.47 | 12 | 7.31 | 18.7191 | YES | 350
30 | 0.88 | 179 | 157.52 | 12.4 | 7.29 | 18.0168 | YES | 350
| 0 | 0 | 0 | 0 | 0 | 0
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2