## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lane
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2021-02-01
System Name: | Rainbow Water District |  |  | ID#: 4100839 |  | WTP ID: TP- | Chase
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 116 |  | 15 | 25 | 0.017 | 0.02
2 | 117 |  | 15.3 | 25 | 0.01 | 0.018
3 | 116 |  | 15.4 | 25 | 0.017 | 0.02
4 | 117 |  | 15.4 | 25 | 0.015 | 0.015
5 | 118 |  | 15.4 | 25 | 0.013 | 0.016
6 | 117 |  | 15.5 | 25 | 0.02 | 0.018
7 | 115 |  | 15.7 | 25 | 0.012 | 0.017
8 | 117 |  | 15.6 | 25 | 0.019 | 0.02
9 | 116 |  | 15.6 | 25 | 0.01 | 0.02
10 | 117 |  | 16 | 25 | 0.015 | 0.019
11 | offline |  | offline | 25 | offline | offline
12 | 113 |  | 12.6 | 25 | 0.03 | 0.033
13 | 116 |  | 14.6 | 25 | 0.02 | 0.02
14 | 118 |  | 15.8 | 25 | 0.027 | 0.027
15 | 118 |  | 16 | 25 | 0.02 | 0.02
16 | 117 |  | 16.6 | 25 | 0.03 | 0.038
17 | 118 |  | 17 | 25 | 0.022 | 0.026
18 | 117 |  | 16.8 | 25 | 0.02 | 0.02
19 | 119 |  | 16.9 | 25 | 0.03 | 0.026
20 | 118 |  | 17.1 | 25 | 0.02 | 0.027
21 | 118 |  | 17.1 | 25 | 0.02 | 0.022
22 | 117 |  | 17.3 | 25 | 0.02 | 0.02
23 | 118 |  | 17.1 | 25 | 0.02 | 0.02
24 | 113 |  | 12.3 | 25 | 0.03 | 0.026
25 | 116 |  | 14.2 | 25 | 0.02 | 0.02
26 | 116 |  | 14.5 | 25 | 0.017 | 0.023
27 | 115 |  | 15.2 | 25 | 0.017 | 0.02
28 | 116 |  | 15.5 | 25 | 0.015 | 0.016
29
30
31
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:Eric Carlson
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE:3/9/21
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 541 ) 954-9941 |  | CERT #:T-09011
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Chase
System Name: | Rainbow Water District |  | ID#: 41 00839 |  | Month/Year: | 2021-02-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.65 | 168.37 | 109.4405 | 13.9 | 6.81 | 26.2472 | YES | 487
2 | 0.67 | 167.75 | 112.3925 | 13.6 | 6.8 | 26.7418 | YES | 488.8
3 | 0.69 | 168.72 | 116.4168 | 13.6 | 6.8 | 26.803 | YES | 486
4 | 0.69 | 167.96 | 115.8924 | 13.6 | 6.8 | 26.803 | YES | 488.2
5 | 0.35 | 167.62 | 58.667 | 13.3 | 6.8 | 26.3038 | YES | 489.2
6 | 0.65 | 168.03 | 109.2195 | 13.3 | 6.81 | 27.3235 | YES | 488
7 | 0.66 | 168.44 | 111.1704 | 13.3 | 6.81 | 27.3548 | YES | 486.8
8 | 0.67 | 168.3 | 112.761 | 13.2 | 6.8 | 27.4677 | YES | 487.2
9 | 0.65 | 167.69 | 108.9985 | 13.1 | 6.8 | 27.589 | YES | 489
10 | 0.65 | 168.38 | 109.447 | 13.5 | 6.78 | 26.6609 | YES | 487
11 | offline | offline | #VALUE! | offline | offline | #VALUE! | #VALUE! | offline
12 | 0.64 | 169.14 | 108.2496 | 13.8 | 6.8 | 26.2954 | YES | 484.8
13 | 0.68 | 167.41 | 113.8388 | 13.6 | 6.8 | 26.7724 | YES | 489.8
14 | 0.67 | 169.07 | 113.2769 | 12.7 | 6.8 | 28.402 | YES | 485
15 | 0.66 | 167.41 | 110.4906 | 13.3 | 6.81 | 27.3548 | YES | 489.8
16 | 0.67 | 168.45 | 112.8615 | 13.1 | 6.83 | 27.9621 | YES | 486.8
17 | 0.69 | 167.86 | 115.8234 | 13.3 | 6.81 | 27.4487 | YES | 488.5
18 | 0.68 | 167.96 | 114.2128 | 13.3 | 6.81 | 27.4174 | YES | 488.2
19 | 0.68 | 168.3 | 114.444 | 12.6 | 6.8 | 28.6252 | YES | 487.2
20 | 0.69 | 167.75 | 115.7475 | 12.6 | 6.78 | 28.4459 | YES | 488.8
21 | 0.69 | 168.72 | 116.4168 | 12.7 | 6.79 | 28.3614 | YES | 486
22 | 0.67 | 168.2 | 112.694 | 12.8 | 6.81 | 28.3177 | YES | 487.5
23 | 0.69 | 168.72 | 116.4168 | 12.8 | 6.81 | 28.3824 | YES | 486
24 | 0.67 | 167.62 | 112.3054 | 13.1 | 6.79 | 27.5495 | YES | 489.2
25 | 0.73 | 167.96 | 122.6108 | 12.9 | 6.81 | 28.3223 | YES | 488.2
26 | 0.67 | 167.76 | 112.3992 | 12.9 | 6.82 | 28.2336 | YES | 488.8
27 | 0.66 | 167.96 | 110.8536 | 13.5 | 6.82 | 27.0915 | YES | 488.2
28 | 0.64 | 167.28 | 107.0592 | 13.5 | 6.81 | 26.9293 | YES | 490.2
29
30
31
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2