## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lane
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2021-03-01
System Name: | Rainbow Water District |  |  | ID#: 4100839 |  | WTP ID: TP- | Chase
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 117 |  | 16 | 25 | 0.015 | 0.015
2 | 117 |  | 16 | 25 | 0.013 | 0.019
3 | 116 |  | 15.4 | 25 | 0.01 | 0.68
4 | 116 |  | 15.2 | 25 | 0.01 | 0.019
5 | 117 |  | 15.4 | 25 | 0.01 | 0.02
6 | 117 |  | 15.4 | 25 | 0.01 | 0.02
7 | 116 |  | 15.5 | 25 | 0.01 | 0.0178
8 | 116 |  | 15.6 | 25 | 0.017 | 0.054
9 | 118 |  | 15.7 | 25 | 0.0115 | 0.02
10 | 116 |  | 16 | 25 | 0.015 | 0.016
11 | 116 |  | 15.7 | 25 | 0.017 | 0.019
12 | 116 |  | 15.3 | 25 | 0.017 | 0.02
13 | offline |  | offline | 25 | offline | offline
14 | offline |  | offline | 25 | offline | offline
15 | 101 |  | 0.4 | 25 | 0.02 | 0.22
16 | 102 |  | 0.5 | 25 | 0.019 | 0.02
17 | 101 |  | 0.5 | 25 | 0.017 | 0.02
18 | 101 |  | 0.5 | 25 | 0.017 | 0.02
19 | 102 |  | 0.5 | 25 | 0.017 | 0.02
20 | 102 |  | 0.5 | 25 | 0.02 | 0.02
21 | 101 |  | 0.5 | 25 | 0.017 | 0.02
22 | 103 |  | 0.6 | 25 | 0.017 | 0.02
23 | 102 |  | 0.6 | 25 | 0.017 | 0.02
24 | 102 |  | 0.6 | 25 | 0.017 | 0.02
25 | 101 |  | 0.6 | 25 | 0.017 | 0.02
26 | 101 |  | 0.6 | 25 | 0.017 | 0.02
27 | 101 |  | 0.6 | 25 | 0.017 | 0.02
28 | 102 |  | 0.6 | 25 | 0.017 | 0.02
29 | 101 |  | 0.7 | 25 | 0.017 | 0.02
30 | 103 |  | 0.7 | 25 | 0.017 | 0.02
31 | 103 |  | 0.7 | 25 | 0.017 | 0.02
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:Eric Carlson
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | 2021-04-07
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 541 )954-9941 |  | CERT #:T-09011
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Chase
System Name: | Rainbow Water District |  | ID#: 41 00839 |  | Month/Year: | 2021-03-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.62 | 167.17 | 103.6454 | 13.5 | 6.81 | 26.8677 | YES | 490.5
2 | 0.63 | 167.51 | 105.5313 | 13.5 | 6.83 | 27.0993 | YES | 489.5
3 | 0.62 | 167.51 | 103.8562 | 13.4 | 6.81 | 27.0483 | YES | 489.5
4 | 0.66 | 167.34 | 110.4444 | 13.4 | 6.81 | 27.1723 | YES | 490
5 | 0.64 | 167.34 | 107.0976 | 13.3 | 6.82 | 27.394 | YES | 490
6 | 0.64 | 168.1 | 107.584 | 13.2 | 6.82 | 27.5779 | YES | 487.8
7 | 0.65 | 167.86 | 109.109 | 13.2 | 6.82 | 27.6095 | YES | 488.5
8 | 0.65 | 167.69 | 108.9985 | 13.1 | 6.82 | 27.7948 | YES | 489
9 | 0.63 | 167.62 | 105.6006 | 13.1 | 6.83 | 27.8346 | YES | 489.2
10 | 0.65 | 167.62 | 108.953 | 13.1 | 6.83 | 27.8983 | YES | 489.2
11 | 0.6 | 167.69 | 100.614 | 13.1 | 6.83 | 27.7394 | YES | 489
12 | 0.59 | 167.28 | 98.6952 | 13.1 | 6.82 | 27.6049 | YES | 490.2
13 | offline | offline | #VALUE! | offline | offline | #VALUE! | #VALUE! | offline
14 | offline | offline | #VALUE! | offline | offline | #VALUE! | #VALUE! | offline
15 | 0.46 | 167.75 | 77.165 | 13.8 | 6.82 | 25.9517 | YES | 488.8
16 | 0.62 | 165.05 | 102.331 | 12.8 | 6.85 | 28.5778 | YES | 496.8
17 | 0.58 | 164.26 | 95.2708 | 12.6 | 6.54 | 25.6917 | YES | 499.2
18 | 0.58 | 165.16 | 95.7928 | 12.7 | 6.84 | 28.5323 | YES | 496.5
19 | 0.59 | 167.51 | 98.8309 | 12.9 | 6.84 | 28.1854 | YES | 489.5
20 | 0.59 | 166.05 | 97.9695 | 12.4 | 6.82 | 29.778 | YES | 493.8
21 | 0.61 | 165.99 | 101.2539 | 12.9 | 6.85 | 28.355 | YES | 494
22 | 0.59 | 165.99 | 97.9341 | 12.9 | 6.85 | 28.2903 | YES | 494
23 | 0.59 | 165.82 | 97.8338 | 12.8 | 6.85 | 28.4801 | YES | 494.5
24 | 0.59 | 166.39 | 98.1701 | 12.9 | 6.86 | 28.3956 | YES | 492.8
25 | 0.57 | 164.65 | 93.8505 | 12.9 | 6.85 | 28.2258 | YES | 498
26 | 0.55 | 166.66 | 91.663 | 12.5 | 6.85 | 28.9247 | YES | 492
27 | 0.54 | 165.05 | 89.127 | 12.5 | 6.85 | 28.8917 | YES | 496.8
28 | 0.53 | 167.42 | 88.7326 | 12.5 | 6.85 | 28.8587 | YES | 489.8
29 | 0.52 | 164.49 | 85.5348 | 12.9 | 6.81 | 27.651 | YES | 498.5
30 | 0.52 | 164.49 | 85.5348 | 12.9 | 6.86 | 28.1695 | YES | 499.5
31 | 0.49 | 166.39 | 81.5311 | 12.9 | 6.86 | 28.0731 | YES | 492.8
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2