## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lane
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2021-08-01
System Name: | Rainbow Water District |  |  | ID#: 4100839 |  | WTP ID: TP- | Chase
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 104 |  | 2.1 | 25 | 0.018 | 0.018
2 | 103 |  | 2.1 | 25 | 0.019 | 0.0195
3 | 103 |  | 2.1 | 25 | 0.02 | 0.025
4 | 104 |  | 2.15 | 25 | 0.019 | 0.038
5 | 104 |  | 2 | 25 | 0.019 | 0.022
6 | 103 |  | 2.1 | 25 | 0.02 | 0.02
7 | 104 |  | 1.97 | 25 | 0.0187 | 0.018
8 | 101 |  | 1.98 | 25 | 0.0187 | 0.019
9 | 104 |  | 2.1 | 25 | 0.02 | 0.02
10 | 104 |  | 2.02 | 25 | 0.02 | 0.02
11 | 102 |  | 2 | 25 | 0.02 | 0.022
12 | 103 |  | 2 | 25 | 0.02 | 0.023
13 | 100 |  | 2 | 25 | 0.02 | 0.021
14 | 102 |  | 2 | 25 | 0.02 | 0.021
15 | 103 |  | 2.2 | 25 | 0.02 | 0.03
16 | 105 |  | 2.2 | 25 | 0.019 | 0.023
17 | 104 |  | 2.3 | 25 | 0.019 | 0.041
18 | 105 |  | 2.4 | 25 | 0.019 | 0.02
19 | 104 |  | 2.5 | 25 | 0.019 | 0.02
20 | 105 |  | 2.5 | 25 | 0.019 | 0.019
21 | 103 |  | 2.58 | 25 | 0.0187 | 0.22
22 | 104 |  | 2.7 | 25 | 0.019 | 0.0197
23 | 105 |  | 2.7 | 25 | 0.019 | 0.021
24 | 106 |  | 2.7 | 25 | 0.019 | 0.0221
25 | 105 |  | 2.9 | 25 | 0.019 | 0.0219
26 | 105 |  | 2.9 | 25 | 0.019 | 0.0348
27 | 107 |  | 3.1 | 25 | 0.019 | 0.0197
28 | 105 |  | 3.1 | 25 | 0.019 | 0.0187
29 | 104 |  | 3.1 | 25 | 0.019 | 0.0188
30 | 108 |  | 3.2 | 25 | 0.019 | 0.0219
31 | 106 |  | 3.1 | 25 | 0.019 | 0.0213
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:Eric Carlson
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE:9/9/21
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 541 ) 954-9941 |  | CERT #:T-09011
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Chase
System Name: | Rainbow Water District |  | ID#: 41 00839 |  | Month/Year: | 2021-08-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.61 | 187.42 | 114.3262 | 17 | 6.67 | 20.1246 | YES | 437.5
2 | 0.63 | 185.6 | 116.928 | 17.2 | 6.7 | 20.1257 | YES | 441.8
3 | 0.63 | 186.7 | 117.621 | 17.1 | 6.71 | 20.3385 | YES | 439.2
4 | 0.62 | 185.1 | 114.762 | 17.2 | 6.72 | 20.254 | YES | 443
5 | 0.62 | 184.47 | 114.3714 | 17.2 | 6.67 | 19.8771 | YES | 444.5
6 | 0.63 | 186.27 | 117.3501 | 17.3 | 6.67 | 19.7659 | YES | 440.2
7 | 0.56 | 196.26 | 109.9056 | 17 | 6.66 | 19.9337 | YES | 417.8
8 | 0.59 | 203.72 | 120.1948 | 17.4 | 6.69 | 19.6895 | YES | 402.5
9 | 0.61 | 203.87 | 124.3607 | 17.5 | 6.7 | 19.6757 | YES | 402.2
10 | 0.6 | 204.48 | 122.688 | 17.7 | 6.69 | 19.3158 | YES | 401
11 | 0.56 | 204.5 | 114.52 | 17.7 | 6.71 | 19.3719 | YES | 400.8
12 | 0.57 | 202.97 | 115.6929 | 17.7 | 6.71 | 19.3943 | YES | 404
13 | 0.56 | 203.98 | 114.2288 | 17.7 | 6.71 | 19.3719 | YES | 402
14 | 0.57 | 204.23 | 116.4111 | 17.7 | 6.71 | 19.3943 | YES | 401.5
15 | 0.52 | 203.07 | 105.5964 | 17.8 | 6.71 | 19.1522 | YES | 403.8
16 | 0.45 | 200.48 | 90.216 | 17.9 | 6.71 | 18.8693 | YES | 409
17 | 0.59 | 200.88 | 118.5192 | 17.8 | 6.71 | 19.308 | YES | 408.2
18 | 0.64 | 202.71 | 129.7344 | 17.8 | 6.7 | 19.347 | YES | 404.5
19 | 0.61 | 200.88 | 122.5368 | 17.8 | 6.71 | 19.3527 | YES | 408.2
20 | 0.61 | 200 | 122 | 17.9 | 6.71 | 19.222 | YES | 410
21 | 0.61 | 200.98 | 122.5978 | 17.6 | 6.69 | 19.4696 | YES | 408
22 | 0.61 | 200.73 | 122.4453 | 17.6 | 6.71 | 19.6166 | YES | 408.5
23 | 0.62 | 201.47 | 124.9114 | 17.7 | 6.71 | 19.5068 | YES | 407
24 | 0.62 | 199.42 | 123.6404 | 17.8 | 6.71 | 19.3751 | YES | 411.2
25 | 0.61 | 201.97 | 123.2017 | 17.7 | 6.71 | 19.4842 | YES | 406
26 | 0.5 | 197.59 | 98.795 | 17.9 | 6.72 | 19.0504 | YES | 415
27 | 0.63 | 198.07 | 124.7841 | 17.9 | 6.71 | 19.2666 | YES | 414
28 | 0.62 | 196.55 | 121.861 | 17.7 | 6.71 | 19.5068 | YES | 417.2
29 | 0.62 | 196.08 | 121.5696 | 17.5 | 6.66 | 19.4044 | YES | 418.2
30 | 0.62 | 197.02 | 122.1524 | 17.8 | 6.71 | 19.3751 | YES | 416.2
31 | 0.61 | 195 | 118.95 | 17.6 | 6.71 | 19.6166 | YES | 420.5
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2