## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lane
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2022-03-01
System Name: | Rainbow Water District |  |  | ID#: 4100839 |  | WTP ID: TP- | Chase
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 118 |  | 1.7 | 25 | 0.027 | 0.029
2 | 120 |  | 1.7 | 25 | 0.03 | 0.033
3 | 120 |  | 1.8 | 25 | 0.033 | 0.035
4 | 124 |  | 1.9 | 25 | 0.03 | 0.055
5 | 120 |  | 2.1 | 25 | 0.026 | 0.034
6 | 120 |  | 2.2 | 25 | 0.027 | 0.027
7 | 122 |  | 2.2 | 25 | 0.026 | 0.027
8 | 126 |  | 2.2 | 25 | 0.03 | 0.027
9 | 126 |  | 2.2 | 25 | 0.026 | 0.033
10 | 126 |  | 2.2 | 25 | 0.03 | 0.032
11 | 125 |  | 1.9 | 25 | 0.028 | 0.027
12 | 126 |  | 1.9 | 25 | 0.028 | 0.027
13 | 128 |  | 1.9 | 25 | 0.027 | 0.027
14 | 129 |  | 1.9 | 25 | 0.026 | 0.027
15 | 129 |  | 2 | 25 | 0.026 | 0.027
16 | 124 |  | 2.1 | 25 | 0.035 | 0.035
17 | 126 |  | 1.8 | 25 | 0.035 | 0.035
18 | 127 |  | 2 | 25 | 0.028 | 0.033
19 | 102 |  | 2.3 | 25 | 0.026 | 0.033
20 | 102 |  | 2.4 | 25 | 0.026 | 0.035
21 | 103 |  | 2.5 | 25 | 0.026 | 0.035
22 | 103 |  | 2.5 | 25 | 0.026 | 0.03
23 | 104 |  | 2.4 | 25 | 0.026 | 0.031
24 | 103 |  | 2.4 | 25 | 0.026 | 0.03
25 | 103 |  | 2.5 | 25 | 0.026 | 0.029
26 | 104 |  | 2.6 | 25 | 0.027 | 0.027
27 | 104 |  | 2.6 | 25 | 0.026 | 0.031
28 | 104 |  | 2.6 | 25 | 0.026 | 0.026
29 | 104 |  | 2.6 | 25 | 0.026 | 0.027
30 | 104 |  | 2.7 | 25 | 0.027 | 0.0275
31 | 104 |  | 2.7 | 25 | 0.02 | 0.097
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Eric Carlson
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE: 4/8/22
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 541 ) 954-9941 |  | CERT #: T-09011
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Chase
System Name: | Rainbow Water District |  | ID#: 41 00839 |  | Month/Year: | 2022-03-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.58 | 187.55 | 108.779 | 11.6 | 6.69 | 29.9466 | YES | 437.2
2 | 0.49 | 188.15 | 92.1935 | 11.7 | 6.67 | 29.2786 | YES | 435.8
3 | 0.54 | 187.64 | 101.3256 | 11.5 | 6.67 | 29.8061 | YES | 437
4 | 0.55 | 188.15 | 103.4825 | 11.4 | 6.7 | 30.3284 | YES | 435.8
5 | 0.5 | 187.6 | 93.8 | 12.2 | 6.66 | 28.3174 | YES | 437
6 | 0.59 | 168.7 | 99.533 | 12 | 6.66 | 28.948 | YES | 486
7 | 0.6 | 168.2 | 100.92 | 11.9 | 6.68 | 29.3548 | YES | 487.5
8 | 0.59 | 169 | 99.71 | 11.9 | 6.66 | 29.129 | YES | 485.2
9 | 0.59 | 167.86 | 99.0374 | 11.9 | 6.67 | 29.226 | YES | 488.5
10 | 0.59 | 168.2 | 99.238 | 12 | 6.68 | 29.141 | YES | 487.5
11 | 0.56 | 169 | 94.64 | 11.6 | 6.7 | 29.9824 | YES | 485.2
12 | 0.54 | 187.42 | 101.2068 | 11.8 | 6.68 | 29.3498 | YES | 437.5
13 | 0.55 | 187.55 | 103.1525 | 11.4 | 6.66 | 29.9256 | YES | 437.2
14 | 0.55 | 188.28 | 103.554 | 11.4 | 6.71 | 30.4301 | YES | 435.5
15 | 0.51 | 213.54 | 108.9054 | 11.3 | 6.67 | 30.0851 | YES | 384
16 | 0.48 | 212.33 | 101.9184 | 11.5 | 6.69 | 29.8133 | YES | 386.2
17 | 0.4 | 210.14 | 84.056 | 11.3 | 6.68 | 29.8315 | YES | 390.2
18 | 0.29 | 166.26 | 48.2154 | 11.7 | 6.68 | 28.7555 | YES | 493.2
19 | 0.54 | 166.59 | 89.9586 | 11.8 | 6.68 | 29.3498 | YES | 492.2
20 | 0.58 | 165.99 | 96.2742 | 11.8 | 6.86 | 31.3061 | YES | 494
21 | 0.59 | 166.66 | 98.3294 | 11.8 | 6.69 | 29.6057 | YES | 492
22 | 0.6 | 166.73 | 100.038 | 11.9 | 6.68 | 29.3548 | YES | 491.8
23 | 0.59 | 164.62 | 97.1258 | 11.8 | 6.65 | 29.2141 | YES | 498.1
24 | 0.58 | 166.66 | 96.6628 | 11.7 | 6.69 | 29.7597 | YES | 492
25 | 0.59 | 166.66 | 98.3294 | 11.9 | 6.69 | 29.4212 | YES | 492
26 | 0.6 | 167.17 | 100.302 | 11.9 | 6.68 | 29.3548 | YES | 490.5
27 | 0.59 | 163.73 | 96.6007 | 11.8 | 6.66 | 29.3114 | YES | 500.8
28 | 0.58 | 167 | 96.86 | 11.8 | 6.63 | 28.9895 | YES | 491
29 | 0.6 | 165.92 | 99.552 | 11.8 | 6.67 | 29.4406 | YES | 494.2
30 | 0.6 | 166.06 | 99.636 | 11.8 | 6.7 | 29.7364 | YES | 493.8
31 | 0.6 | 167.07 | 100.242 | 11.8 | 6.7 | 29.7364 | YES | 490.8
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2