## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lane
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2022-09-01
System Name: | Rainbow Water District |  |  | ID#: 4100839 |  | WTP ID: TP- | Chase
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 124 |  | 19.4 | 25 | 0.014 | 0.0143
2 | 124 |  | 19.5 | 25 | 0.015 | 0.015
3 | 126 |  | 19.6 | 25 | 0.015 | 0.015
4 | 124 |  | 18.5 | 25 | 0.015 | 0.015
5 | 125 |  | 18.5 | 25 | 0.015 | 0.015
6 | 126 |  | 19 | 25 | 0.015 | 0.015
7 | 126 |  | 19 | 25 | 0.015 | 0.019
8 | 126 |  | 19 | 25 | 0.014 | 0.014
9 | 125 |  | 18.7 | 25 | 0.02 | 0.09
10 | 128 |  | 19 | 25 | 0.015 | 0.017
11 | 128 |  | 20 | 25 | 0.015 | 0.017
12 | 132 |  | 22.6 | 25 | 0.015 | 0.015
13 | 110 |  | 0.33 | 25 | 0.081 | 0.112
14 | 112 |  | 0.41 | 25 | 0.057 | 0.815
15 | 113 |  | 0.45 | 25 | 0.063 | 0.07
16 | 113 |  | 0.5 | 25 | 0.053 | 0.08
17 | 114 |  | 0.55 | 25 | 0.079 | 0.08
18 | 100 |  | 0.5 | 25 | 0.02 | 0.143
19 | 118 |  | 0.48 | 25 | 0.026 | 0.0412
20 | 119 |  | 0.47 | 25 | 0.024 | 0.028
21 | 119 |  | 0.5 | 25 | 0.035 | 0.036
22 | offline |  | offline | 25 | offline | offline
23 | offline |  | offline | 25 | offline | offline
24 | offline |  | offline | 25 | offline | offline
25 | offline |  | offline | 25 | offline | offline
26 | 112 |  | 0.42 | 25 | 0.063 | 0.063
27 | 117 |  | 0.5 | 25 | 0.034 | 0.041
28 | 118 |  | 0.51 | 25 | 0.039 | 0.047
29 | 118 |  | 0.5 | 25 | 0.041 | 0.043
30 | 121 |  | 0.49 | 25 | 0.043 | 0.047
31
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Eric Carlson
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE: 10/7/22
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 541 ) 954-9941 |  | CERT #: T-09011
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Chase
System Name: | Rainbow Water District |  | ID#: 4100839 |  | Month/Year: | 2022-09-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.55 | 175.66 | 96.613 | 15.8 | 6.25 | 18.5092 | YES | 466.8
2 | 0.55 | 173.91 | 95.6505 | 15.8 | 6.37 | 19.3648 | YES | 471.5
3 | 0.5 | 175.66 | 87.83 | 15.8 | 6.36 | 19.1808 | YES | 466.8
4 | 0.49 | 187.72 | 91.9828 | 15.9 | 6.38 | 19.173 | YES | 436.8
5 | 0.5 | 187.55 | 93.775 | 16 | 6.37 | 18.9939 | YES | 437.2
6 | 0.47 | 186.87 | 87.8289 | 16.2 | 6.37 | 18.673 | YES | 438.8
7 | 0.47 | 187.42 | 88.0874 | 15.9 | 6.37 | 19.0568 | YES | 437.5
8 | 0.5 | 188.28 | 94.14 | 15.9 | 6.36 | 19.0512 | YES | 435.5
9 | 0.55 | 186.57 | 102.6135 | 15.7 | 6.37 | 19.4964 | YES | 439.5
10 | 0.53 | 186.44 | 98.8132 | 15.9 | 6.3 | 18.6904 | YES | 439.8
11 | 0.5 | 187.3 | 93.65 | 16 | 6.37 | 18.9939 | YES | 437.8
12 | 0.46 | 177.87 | 81.8202 | 16 | 6.37 | 18.9061 | YES | 461
13 | 0.23 | 168.44 | 38.7412 | 16.1 | 6.37 | 18.2844 | YES | 486.8
14 | 0.6 | 166.5 | 99.9 | 15.8 | 6.36 | 19.404 | YES | 492.5
15 | 0.59 | 167.42 | 98.7778 | 15.5 | 6.3 | 19.338 | YES | 489.8
16 | 0.59 | 167.51 | 98.8309 | 15.7 | 6.37 | 19.5868 | YES | 489.5
17 | 0.58 | 167.34 | 97.0572 | 15.6 | 6.36 | 19.6231 | YES | 490
18 | 0.58 | 167.17 | 96.9586 | 15.3 | 6.36 | 20.0256 | YES | 490.5
19 | 0.58 | 168.3 | 97.614 | 15.6 | 6.37 | 19.6971 | YES | 487.2
20 | 0.59 | 167.86 | 99.0374 | 15.4 | 6.32 | 19.6164 | YES | 488.5
21 | 0.61 | 167.41 | 102.1201 | 15.5 | 6.34 | 19.6766 | YES | 489.8
22 | offline | offline | #VALUE! | offline | offline | #VALUE! | #VALUE! | offline
23 | offline | offline | #VALUE! | offline | offline | #VALUE! | #VALUE! | offline
24 | offline | offline | #VALUE! | offline | offline | #VALUE! | #VALUE! | offline
25 | offline | offline | #VALUE! | offline | offline | #VALUE! | #VALUE! | offline
26 | 0.52 | 168.1 | 87.412 | 14.8 | 6.43 | 21.1185 | YES | 487.8
27 | 0.73 | 167.68 | 122.4064 | 15.2 | 6.37 | 20.5909 | YES | 489
28 | 0.66 | 167.41 | 110.4906 | 15.2 | 6.27 | 19.6721 | YES | 489
29 | 0.69 | 166.32 | 114.7608 | 15.2 | 6.37 | 20.496 | YES | 493
30 | 0.64 | 166.83 | 106.7712 | 15.2 | 6.35 | 20.2256 | YES | 491.5
31
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2