## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lane
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2022-11-01
System Name: | Rainbow Water District |  |  | ID#: 4100839 |  | WTP ID: TP- | Chase
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 104 |  | 1.18 | 25 | 0.019 | 0.021
2 | Offline |  | Offline | 25 | Offline | Offline
3 | 103 |  | 1.1 | 25 | 0.021 | 0.028
4 | 103 |  | 1.1 | 25 | 0.017 | 0.021
5 | 103 |  | 1.14 | 25 | 0.02 | 0.145
6 | 106 |  | 2.26 | 25 | 0.1 | 0.145
7 | 107 |  | 2.59 | 25 | 0.052 | 0.07
8 | 105 |  | 2.42 | 25 | 0.039 | 0.044
9 | 106 |  | 2.38 | 25 | 0.024 | 0.033
10 | 107 |  | 2.73 | 25 | 0.028 | 0.033
11 | 107 |  | 2.5 | 25 | 0.022 | 0.025
12 | 106 |  | 2.55 | 25 | 0.025 | 0.027
13 | 105 |  | 2.47 | 25 | 0.02 | 0.022
14 | 108 |  | 2.6 | 25 | 0.02 | 0.02
15 | 108 |  | 2.6 | 25 | 0.017 | 0.02
16 | 108 |  | 2.65 | 25 | 0.017 | 0.02
17 | 107 |  | 2.8 | 25 | 0.017 | 0.021
18 | 108 |  | 2.8 | 25 | 0.02 | 0.021
19 | 107 |  | 2.7 | 25 | 0.02 | 0.027
20 | 110 |  | 2.8 | 25 | 0.02 | 0.021
21 | 111 |  | 2.8 | 25 | 0.02 | 0.027
22 | 111 |  | 2.9 | 25 | 0.027 | 0.027
23 | 110 |  | 2.8 | 25 | 0.02 | 0.024
24 | 110 |  | 3 | 25 | 0.02 | 0.027
25 | 112 |  | 3 | 25 | 0.027 | 0.027
26 | 112 |  | 2.97 | 25 | 0.023 | 0.027
27 | 111 |  | 3.1 | 25 | 0.019 | 0.176
28 | 114 |  | 3.1 | 25 | 0.019 | 0.021
29 | 112 |  | 3.1 | 25 | 0.021 | 0.027
30 | 114 |  | 3 | 25 | 0.02 | 0.027
31
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Eric Carlson
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE: 12/5/22
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 541 ) 954-9941 |  | CERT #: T-09011
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Chase
System Name: | Rainbow Water District |  | ID#: 41 00839 |  | Month/Year: | 2022-11-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.6 | 166.59 | 99.954 | 14.6 | 6.38 | 21.2027 | YES | 492.2
2 | Offline | Offline | #VALUE! | Offline | Offline | #VALUE! | #VALUE! | Offline
3 | 0.47 | 166.73 | 78.3631 | 14.6 | 6.36 | 20.7311 | YES | 491.8
4 | 0.65 | 167.34 | 108.771 | 14.6 | 6.36 | 21.166 | YES | 490
5 | 0.58 | 167.62 | 97.2196 | 14.5 | 6.36 | 21.1381 | YES | 489.2
6 | 0.57 | 167.75 | 95.6175 | 14.5 | 6.39 | 21.3525 | YES | 488.8
7 | 0.57 | 166.63 | 94.9791 | 14.3 | 6.37 | 21.481 | YES | 491.7
8 | 0.46 | 168.03 | 77.2938 | 14.7 | 6.36 | 20.5678 | YES | 488
9 | 0.59 | 166.32 | 98.1288 | 14.6 | 6.37 | 21.099 | YES | 493
10 | 0.59 | 167.27 | 98.6893 | 14.5 | 6.37 | 21.2419 | YES | 490.2
11 | 0.59 | 166.16 | 98.0344 | 14.4 | 6.39 | 21.5467 | YES | 493.5
12 | 0.6 | 166.16 | 99.696 | 14.4 | 6.35 | 21.2505 | YES | 493.5
13 | 0.59 | 167.51 | 98.8309 | 14.4 | 6.36 | 21.3058 | YES | 489.5
14 | 0.59 | 166.83 | 98.4297 | 14.2 | 6.39 | 21.8393 | YES | 491.5
15 | 0.59 | 167 | 98.53 | 14.3 | 6.38 | 21.6114 | YES | 491
16 | 0.6 | 166.83 | 100.098 | 14.3 | 6.39 | 21.7175 | YES | 491.5
17 | 0.6 | 167.41 | 100.446 | 14.3 | 6.39 | 21.7175 | YES | 489.8
18 | 0.6 | 165.25 | 99.15 | 13.9 | 6.4 | 22.3947 | YES | 496.2
19 | 0.6 | 166.93 | 100.158 | 13.9 | 6.39 | 22.3111 | YES | 491.2
20 | 0.6 | 167.51 | 100.506 | 13.9 | 6.34 | 21.8974 | YES | 489.5
21 | 0.59 | 168.44 | 99.3796 | 13.8 | 6.39 | 22.436 | YES | 486.8
22 | 0.62 | 167 | 103.54 | 13.7 | 6.38 | 22.5811 | YES | 491
23 | 0.62 | 168.2 | 104.284 | 13.9 | 6.39 | 22.3625 | YES | 487.5
24 | 0.36 | 168.1 | 60.516 | 13.6 | 6.42 | 22.3966 | YES | 487.8
25 | 0.54 | 166.49 | 89.9046 | 13.6 | 6.43 | 22.9507 | YES | 492.5
26 | 0.56 | 168.37 | 94.2872 | 13.6 | 6.39 | 22.662 | YES | 487
27 | 0.56 | 168.1 | 94.136 | 13.7 | 6.43 | 22.8491 | YES | 487.8
28 | 0.55 | 167.27 | 91.9985 | 13.5 | 6.42 | 23.0459 | YES | 490.2
29 | 0.56 | 167.62 | 93.8672 | 13.4 | 6.44 | 23.4024 | YES | 489.2
30 | 0.56 | 167.68 | 93.9008 | 13.6 | 6.44 | 23.0896 | YES | 489
31
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2