## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lane
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2023-01-01
System Name: | Rainbow Water District |  |  | ID#: 4100839 |  | WTP ID: TP- | Chase
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 114 |  | 12.7 | 25 | 0.083 | 0.1
2 | 115 |  | 13.3 | 25 | 0.042 | 0.058
3 | 116 |  | 13.7 | 25 | 0.027 | 0.043
4 | 117 |  | 14.9 | 25 | 0.021 | 0.027
5 | 118 |  | 14.5 | 25 | 0.019 | 0.021
6 | 116 |  | 15.2 | 25 | 0.019 | 0.024
7 | 117 |  | 15.3 | 25 | 0.019 | 0.021
8 | 117 |  | 15.3 | 25 | 0.02 | 0.022
9 | 118 |  | 15.9 | 25 | 0.019 | 0.02
10 | 118 |  | 16 | 25 | 0.017 | 0.021
11 | 117 |  | 16 | 25 | 0.02 | 0.021
12 | 117 |  | 16.3 | 25 | 0.02 | 0.021
13 | 117 |  | 16.4 | 25 | 0.02 | 0.025
14 | 118 |  | 16.3 | 25 | 0.017 | 0.02
15 | 119 |  | 16.4 | 25 | 0.02 | 0.028
16 | 121 |  | 16.5 | 25 | 0.017 | 0.02
17 | 120 |  | 16.6 | 25 | 0.017 | 0.02
18 | 118 |  | 17 | 25 | 0.017 | 0.02
19 | 119 |  | 16.8 | 25 | 0.017 | 0.021
20 | offline |  | offline | 25 | offline | offline
21 | offline |  | offline | 25 | offline | offline
22 | offline |  | offline | 25 | offline | offline
23 | offline |  | offline | 25 | offline | offline
24 | 115 |  | 11.9 | 25 | 0.027 | 0.03
25 | 114 |  | 11.9 | 25 | 0.021 | 0.023
26 | 114 |  | 13.3 | 25 | 0.021 | 0.021
27 | 116 |  | 13.5 | 25 | 0.015 | 0.019
28 | 115 |  | 13.8 | 25 | 0.021 | 0.021
29 | 117 |  | 14.5 | 25 | 0.021 | 0.021
30 | 119 |  | 14.6 | 25 | 0.017 | 0.036
31 | 118 |  | 15.3 | 25 | 0.015 | 0.017
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Eric Carlson
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE: 2/3/23
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 541 ) 954-9941 |  | CERT #: T-09011
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Chase
System Name: | Rainbow Water District |  | ID#: 41 00839 |  | Month/Year: | 2023-01-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.52 | 174.02 | 90.4904 | 11.4 | 6.46 | 27.9139 | YES | 471.2
2 | 0.52 | 175.51 | 91.2652 | 11.4 | 6.46 | 27.9139 | YES | 467.2
3 | 0.54 | 174.54 | 94.2516 | 11.6 | 6.46 | 27.6292 | YES | 469.8
4 | 0.54 | 172.99 | 93.4146 | 11.7 | 6.45 | 27.3689 | YES | 474
5 | 0.51 | 174.02 | 88.7502 | 12.1 | 6.44 | 26.5322 | YES | 471.2
6 | 0.49 | 174.09 | 85.3041 | 11.9 | 6.45 | 26.8916 | YES | 471
7 | 0.6 | 173.8 | 104.28 | 11.9 | 6.43 | 27.0272 | YES | 471.8
8 | 0.57 | 174.84 | 99.6588 | 12 | 6.39 | 26.4288 | YES | 469
9 | 0.58 | 173.91 | 100.8678 | 11.9 | 6.44 | 27.0589 | YES | 471.5
10 | 0.59 | 172.08 | 101.5272 | 12 | 6.45 | 27.0097 | YES | 476.5
11 | 0.6 | 174.39 | 104.634 | 11.9 | 6.42 | 26.9388 | YES | 470.2
12 | 0.6 | 175.51 | 105.306 | 12.1 | 6.41 | 26.5229 | YES | 467.2
13 | 0.58 | 170.3 | 98.774 | 12 | 6.38 | 26.3703 | YES | 481.5
14 | 0.58 | 175.4 | 101.732 | 11.8 | 6.44 | 27.2261 | YES | 467.5
15 | 0.57 | 170.83 | 97.3731 | 11.8 | 6.38 | 26.6677 | YES | 480.6
16 | 0.61 | 174.65 | 106.5365 | 11.8 | 6.44 | 27.3125 | YES | 469.5
17 | 0.64 | 176.15 | 112.736 | 11.8 | 6.43 | 27.3093 | YES | 465.5
18 | 0.64 | 176.55 | 112.992 | 11.9 | 6.43 | 27.1415 | YES | 469.5
19 | 0.65 | 176.53 | 114.7445 | 12.2 | 6.4 | 26.4131 | YES | 464.5
20 | offline | offline | #VALUE! | offline | offline | #VALUE! | #VALUE! | offline
21 | offline | offline | #VALUE! | offline | offline | #VALUE! | #VALUE! | offline
22 | offline | offline | #VALUE! | offline | offline | #VALUE! | #VALUE! | offline
23 | offline | offline | #VALUE! | offline | offline | #VALUE! | #VALUE! | offline
24 | 0.63 | 177.56 | 111.8628 | 13 | 6.36 | 23.5211 | YES | 461.8
25 | 0.68 | 176.91 | 120.2988 | 11.8 | 6.4 | 27.1559 | YES | 463.5
26 | 0.67 | 177.41 | 118.8647 | 11.75 | 6.41 | 27.3005 | YES | 462.2
27 | 0.64 | 176.15 | 112.736 | 12.2 | 6.41 | 26.4717 | YES | 465.5
28 | 0.64 | 177.29 | 113.4656 | 11.8 | 6.37 | 26.777 | YES | 462.5
29 | 0.65 | 174.91 | 113.6915 | 11.6 | 6.41 | 27.4962 | YES | 468.8
30 | 0.67 | 177.68 | 119.0456 | 11.7 | 6.43 | 27.5656 | YES | 461.5
31 | 0.67 | 176.34 | 118.1478 | 11.7 | 6.45 | 27.7478 | YES | 465
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2