## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lane
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2023-02-01
System Name: | Rainbow Water District |  |  | ID#: 4100839 |  | WTP ID: TP- | Chase
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 120 |  | 15.9 | 25 | 0.012 | 0.02
2 | 118 |  | 16.4 | 25 | 0.012 | 0.019
3 | 120 |  | 16.2 | 25 | 0.014 | 0.018
4 | 118 |  | 16.8 | 25 | 0.015 | 0.017
5 | 119 |  | 16.8 | 25 | 0.013 | 0.013
6 | 120 |  | 16.8 | 25 | 0.015 | 0.014
7 | 119 |  | 16.7 | 25 | 0.014 | 0.016
8 | 120 |  | 17 | 25 | 0.015 | 0.013
9 | 120 |  | 16.3 | 25 | 0.015 | 0.015
10 | 121 |  | 17.1 | 25 | 0.015 | 0.015
11 | 119 |  | 17.2 | 25 | 0.013 | 0.013
12 | 122 |  | 17.5 | 25 | 0.013 | 0.013
13 | 121 |  | 18 | 25 | 0.014 | 0.013
14 | 121 |  | 17.8 | 25 | 0.014 | 0.018
15 | 122 |  | 18.3 | 25 | 0.015 | 0.015
16 | 121 |  | 18.2 | 25 | 0.013 | 0.013
17 | 122 |  | 18.5 | 25 | 0.013 | 0.014
18 | 122 |  | 18.5 | 25 | 0.013 | 0.014
19 | 122 |  | 18.5 | 25 | 0.013 | 0.014
20 | 122 |  | 18.5 | 25 | 0.013 | 0.014
21 | 123 |  | 19 | 25 | 0.014 | 0.014
22 | 122 |  | 18.3 | 25 | 0.017 | 0.02
23 | 122 |  | 18.5 | 25 | 0.013 | 0.014
24 | 122 |  | 18.7 | 25 | 0.012 | 0.014
25 | 123 |  | 19.5 | 25 | 0.013 | 0.014
26 | 122 |  | 19.9 | 25 | 0.013 | 0.014
27 | 124 |  | 20 | 25 | 0.013 | 0.016
28 | 124 |  | 20.4 | 25 | 0.013 | 0.014
29
30
31
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Eric Carlson
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE: 3/3/23
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 541 ) 954-9941 |  | CERT #: T-09011
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Chase
System Name: | Rainbow Water District |  | ID#: 41 00839 |  | Month/Year: | 2023-02-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.67 | 177.29 | 118.7843 | 11.57 | 6.47 | 28.1573 | YES | 462.5
2 | 0.65 | 177.68 | 115.492 | 11.48 | 6.43 | 27.8841 | YES | 461.5
3 | 0.64 | 177.02 | 113.2928 | 11.45 | 6.41 | 27.7229 | YES | 463.2
4 | 0.62 | 177.1 | 109.802 | 11.6 | 6.45 | 27.7725 | YES | 463
5 | 0.63 | 178.26 | 112.3038 | 11.8 | 6.4 | 27.0131 | YES | 460
6 | 0.67 | 177.95 | 119.2265 | 11.5 | 6.45 | 28.0936 | YES | 460.8
7 | 0.37 | 177.29 | 65.5973 | 11.48 | 6.42 | 26.9821 | YES | 462.2
8 | 0.62 | 177.87 | 110.2794 | 11.6 | 6.44 | 27.6811 | YES | 461
9 | 0.58 | 176.8 | 102.544 | 11.7 | 6.44 | 27.3946 | YES | 463.8
10 | 0.61 | 177.48 | 108.2628 | 11.7 | 6.43 | 27.3913 | YES | 462
11 | 0.63 | 177.68 | 111.9384 | 11.7 | 6.39 | 27.0909 | YES | 461.5
12 | 0.62 | 177.48 | 110.0376 | 11.2 | 6.41 | 28.0957 | YES | 462
13 | 0.61 | 177.02 | 107.9822 | 11.4 | 6.4 | 27.6294 | YES | 463.2
14 | 0.63 | 177.95 | 112.1085 | 11.68 | 6.41 | 27.303 | YES | 460.8
15 | 0.63 | 177.48 | 111.8124 | 11.6 | 6.44 | 27.7105 | YES | 462
16 | 0.62 | 176.53 | 109.4486 | 11.6 | 6.42 | 27.4995 | YES | 464.5
17 | 0.61 | 177.95 | 108.5495 | 11.6 | 6.44 | 27.6519 | YES | 460.8
18 | 0.61 | 178.06 | 108.6166 | 11.6 | 6.38 | 27.1117 | YES | 460.5
19 | 0.61 | 178.18 | 108.6898 | 11.7 | 6.45 | 27.5721 | YES | 460.2
20 | 0.62 | 177.41 | 109.9942 | 11.6 | 6.44 | 27.6811 | YES | 462.2
21 | 0.61 | 177.87 | 108.5007 | 11.6 | 6.42 | 27.4704 | YES | 461
22 | 0.57 | 178.06 | 101.4942 | 11.6 | 6.46 | 27.717 | YES | 460.5
23 | 0.62 | 177.79 | 110.2298 | 11.6 | 6.43 | 27.5901 | YES | 461.2
24 | 0.63 | 177.87 | 112.0581 | 11.73 | 6.41 | 27.219 | YES | 461
25 | 0.63 | 178.33 | 112.3479 | 11.6 | 6.45 | 27.8019 | YES | 459.8
26 | 0.62 | 178.06 | 110.3972 | 11.5 | 6.43 | 27.7612 | YES | 460.5
27 | 0.6 | 177.11 | 106.266 | 11.5 | 6.43 | 27.7025 | YES | 463
28 | 0.62 | 178.07 | 110.4034 | 11.5 | 6.43 | 27.7612 | YES | 460.5
29
30
31
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2