## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lane
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2023-06-01
System Name: | Rainbow Water District |  |  | ID#: 4100839 |  | WTP ID: TP- | Chase
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 126 |  | 3.3 | 25 | 0.019 | 0.021
2 | 128 |  | 3.3 | 25 | 0.02 | 0.025
3 | 128 |  | 3.4 | 25 | 0.02 | 0.02
4 | 128 |  | 3.5 | 25 | 0.018 | 0.019
5 | 103 |  | 3 | 25 | 0.025 | 0.025
6 | 104 |  | 3.1 | 25 | 0.02 | 0.021
7 | 103 |  | 3.3 | 25 | 0.02 | 0.02
8 | 105 |  | 3.3 | 25 | 0.02 | 0.02
9 | 105 |  | 3.3 | 25 | 0.02 | 0.02
10 | 105 |  | 3.4 | 25 | 0.02 | 0.02
11 | 104 |  | 3.4 | 25 | 0.02 | 0.02
12 | 105 |  | 3.6 | 25 | 0.017 | 0.017
13 | 105 |  | 3.6 | 25 | 0.018 | 0.019
14 | 104 |  | 3.6 | 25 | 0.019 | 0.019
15 | 105 |  | 3.7 | 25 | 0.019 | 0.019
16 | 105 |  | 3.8 | 25 | 0.018 | 0.018
17 | 106 |  | 3.7 | 25 | 0.019 | 0.019
18 | 105 |  | 3.6 | 25 | 0.02 | 0.02
19 | 105 |  | 3.6 | 25 | 0.019 | 0.021
20 | 105 |  | 3.7 | 25 | 0.019 | 0.02
21 | 105 |  | 3.7 | 25 | 0.025 | 0.025
22 | 105 |  | 3.7 | 25 | 0.019 | 0.018
23 | 104 |  | 3.8 | 25 | 0.017 | 0.017
24 | 105 |  | 3.8 | 25 | 0.018 | 0.018
25 | 105 |  | 3.8 | 25 | 0.017 | 0.019
26 | 105 |  | 3.9 | 25 | 0.017 | 0.0187
27 | 105 |  | 3.7 | 25 | 0.017 | 0.0187
28 | 105 |  | 3.8 | 25 | 0.017 | 0.0187
29 | 105 |  | 3.9 | 25 | 0.018 | 0.0187
30 | 105 |  | 4 | 25 | 0.018 | 0.0182
31
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Eric Carlson
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE: 7/6/23
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 541 ) 954-9941 |  | CERT #: T-09011
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Chase
System Name: | Rainbow Water District |  | ID#: 41 00839 |  | Month/Year: | 2023-06-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.59 | 199.12 | 117.4808 | 12.08 | 6.46 | 26.9653 | YES | 411.8
2 | 0.45 | 200 | 90 | 12 | 6.49 | 26.9656 | YES | 410
3 | 0.67 | 199.61 | 133.7387 | 12.2 | 6.4 | 26.4686 | YES | 410.8
4 | 0.67 | 201.47 | 134.9849 | 12.2 | 6.44 | 26.8172 | YES | 407
5 | 0.39 | 177.84 | 69.3576 | 12.3 | 6.46 | 26.051 | YES | 461
6 | 0.48 | 174.84 | 83.9232 | 12.2 | 6.48 | 26.633 | YES | 469
7 | 0.49 | 175.89 | 86.1861 | 12.3 | 6.47 | 26.4115 | YES | 466.2
8 | 0.52 | 176.72 | 91.8944 | 12.3 | 6.46 | 26.4084 | YES | 464
9 | 0.53 | 177.18 | 93.9054 | 12.3 | 6.45 | 26.3499 | YES | 462.8
10 | 0.54 | 176.41 | 95.2614 | 12.2 | 6.42 | 26.2811 | YES | 464.8
11 | 0.53 | 176.41 | 93.4973 | 12.3 | 6.38 | 25.756 | YES | 464.8
12 | 0.54 | 175.89 | 94.9806 | 12.5 | 6.46 | 24.9902 | YES | 466.2
13 | 0.54 | 176.53 | 95.3262 | 12.5 | 6.4 | 24.4372 | YES | 464.5
14 | 0.54 | 174.91 | 94.4514 | 12.5 | 6.47 | 25.0835 | YES | 468.8
15 | 0.56 | 175.28 | 98.1568 | 12.6 | 6.47 | 24.9729 | YES | 467.8
16 | 0.55 | 177.79 | 97.7845 | 12.6 | 6.47 | 24.9443 | YES | 461.2
17 | 0.54 | 176.04 | 95.0616 | 12.6 | 6.27 | 23.1233 | YES | 465.8
18 | 0.56 | 176.04 | 98.5824 | 12.6 | 6.29 | 23.3504 | YES | 465.8
19 | 0.58 | 175.51 | 101.7958 | 12.6 | 6.45 | 24.8443 | YES | 467.2
20 | 0.58 | 173.65 | 100.717 | 12.6 | 6.37 | 24.1138 | YES | 472.2
21 | 0.59 | 174.28 | 102.8252 | 12.7 | 6.43 | 24.5227 | YES | 470.5
22 | 0.53 | 176.15 | 93.3595 | 12.8 | 6.47 | 24.5552 | YES | 464.5
23 | 0.54 | 175.21 | 94.6134 | 13 | 6.41 | 23.7181 | YES | 468
24 | 0.55 | 175.89 | 96.7395 | 13 | 6.43 | 23.9233 | YES | 466.2
25 | 0.55 | 176.53 | 97.0915 | 13 | 6.47 | 24.2831 | YES | 464.5
26 | 0.55 | 175.03 | 96.2665 | 13.2 | 6.48 | 24.0486 | YES | 468.5
27 | 0.54 | 175.4 | 94.716 | 13.2 | 6.4 | 23.3139 | YES | 467.5
28 | 0.54 | 176.34 | 95.2236 | 13.4 | 6.47 | 23.6118 | YES | 465
29 | 0.53 | 175.89 | 93.2217 | 13.5 | 6.47 | 23.4267 | YES | 466.2
30 | 0.53 | 176.34 | 93.4602 | 13.5 | 6.46 | 23.3393 | YES | 465
31
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2