## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lane
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2023-07-01
System Name: | Rainbow Water District |  |  | ID#: 4100839 |  | WTP ID: TP- | Chase
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 104 |  | 3.9 | 25 | 0.019 | 0.019
2 | 104 |  | 3.9 | 25 | 0.017 | 0.018
3 | 105 |  | 3.8 | 25 | 0.019 | 0.019
4 | 104 |  | 4 | 25 | 0.017 | 0.0187
5 | 105 |  | 4 | 25 | 0.017 | 0.0187
6 | 105 |  | 4.1 | 25 | 0.018 | 0.018
7 | 105 |  | 4.1 | 25 | 0.019 | 0.019
8 | 105 |  | 3.9 | 25 | 0.019 | 0.019
9 | 104 |  | 3.9 | 25 | 0.019 | 0.019
10 | 106 |  | 4.1 | 25 | 0.019 | 0.026
11 | 104 |  | 3.7 | 25 | 0.019 | 0.019
12 | 104 |  | 4.1 | 25 | 0.019 | 0.019
13 | 106 |  | 4.2 | 25 | 0.019 | 0.019
14 | 104 |  | 4.2 | 25 | 0.019 | 0.019
15 | 103 |  | 4.2 | 25 | 0.017 | 0.017
16 | 105 |  | 4.2 | 25 | 0.019 | 0.019
17 | 104 |  | 4.2 | 25 | 0.019 | 0.019
18 | 105 |  | 4.3 | 25 | 0.019 | 0.019
19 | 105 |  | 4.3 | 25 | 0.019 | 0.031
20 | 105 |  | 4.4 | 25 | 0.019 | 0.019
21 | 105 |  | 4.4 | 25 | 0.017 | 0.017
22 | 105 |  | 4.4 | 25 | 0.019 | 0.019
23 | 105 |  | 4.4 | 25 | 0.019 | 0.019
24 | 106 |  | 4.5 | 25 | 0.019 | 0.019
25 | 104 |  | 4.6 | 25 | 0.017 | 0.0186
26 | 105 |  | 4.3 | 25 | 0.019 | 0.019
27 | 106 |  | 4.6 | 25 | 0.019 | 0.019
28 | 106 |  | 4.5 | 25 | 0.019 | 0.019
29 | 105 |  | 4.4 | 25 | 0.018 | 0.018
30 | 105 |  | 4.5 | 25 | 0.018 | 0.018
31 | 104 |  | 4.5 | 25 | 0.019 | 0.019
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Eric Carlson
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE: 8/3/23
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 541 ) 954-9941 |  | CERT #: T-09011
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Chase
System Name: | Rainbow Water District |  | ID#: 4100839 |  | July/2023 |  | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.6 | 176.34 | 105.804 | 13.4 | 6.32 | 22.4789 | YES | 465
2 | 0.41 | 176.26 | 72.2666 | 13.5 | 6.35 | 22.0917 | YES | 465.2
3 | 0.56 | 176.8 | 99.008 | 13.7 | 6.45 | 23.0206 | YES | 463.8
4 | 0.56 | 177.8 | 99.568 | 13.7 | 6.39 | 22.5099 | YES | 461.2
5 | 0.58 | 176.72 | 102.4976 | 13.9 | 6.45 | 22.765 | YES | 464
6 | 0.58 | 174.91 | 101.4478 | 14 | 6.46 | 22.697 | YES | 468.8
7 | 0.58 | 176.26 | 102.2308 | 13.9 | 6.27 | 21.2815 | YES | 465.2
8 | 0.61 | 175.77 | 107.2197 | 13.9 | 6.29 | 21.5158 | YES | 466.5
9 | 0.6 | 175.89 | 105.534 | 14 | 6.34 | 21.7502 | YES | 466.2
10 | 0.51 | 176.15 | 89.8365 | 14.1 | 6.46 | 22.3638 | YES | 465.5
11 | 0.5 | 184.77 | 92.385 | 14.2 | 6.48 | 22.3548 | YES | 443.8
12 | 0.5 | 176.65 | 88.325 | 14.3 | 6.45 | 21.9567 | YES | 464.2
13 | 0.6 | 175.78 | 105.468 | 14.4 | 6.46 | 22.1444 | YES | 466.5
14 | 0.59 | 177.18 | 104.5362 | 14.5 | 6.45 | 21.8883 | YES | 467.8
15 | 0.58 | 177.18 | 102.7644 | 14.4 | 6.39 | 21.5219 | YES | 462.8
16 | 0.58 | 174.28 | 101.0824 | 14.6 | 6.4 | 21.3131 | YES | 470.5
17 | 0.58 | 175.78 | 101.9524 | 14.7 | 6.36 | 20.8545 | YES | 466.5
18 | 0.59 | 177.41 | 104.6719 | 14.8 | 6.42 | 21.21 | YES | 462.2
19 | 0.59 | 175.89 | 103.7751 | 14.9 | 6.44 | 21.2258 | YES | 466.2
20 | 0.62 | 175.4 | 108.748 | 14.9 | 6.43 | 21.2197 | YES | 467.5
21 | 0.61 | 175.51 | 107.0611 | 15 | 6.43 | 21.0526 | YES | 467.2
22 | 0.61 | 176.72 | 107.7992 | 14.9 | 6.39 | 20.8797 | YES | 464
23 | 0.6 | 176.34 | 105.804 | 15.1 | 6.42 | 20.8086 | YES | 465
24 | 0.61 | 176.15 | 107.4515 | 15.3 | 6.43 | 20.6303 | YES | 465.5
25 | 0.62 | 176.64 | 109.5168 | 15.1 | 6.29 | 19.8631 | YES | 464.2
26 | 0.6 | 176.65 | 105.99 | 15.2 | 6.29 | 19.6835 | YES | 464.2
27 | 0.6 | 175.4 | 105.24 | 15.4 | 6.44 | 20.5447 | YES | 467.5
28 | 0.61 | 177.18 | 108.0798 | 15.5 | 6.44 | 20.4299 | YES | 462.8
29 | 0.62 | 175.02 | 108.5124 | 15.3 | 6.4 | 20.4229 | YES | 468.5
30 | 0.61 | 176.41 | 107.6101 | 15.5 | 6.39 | 20.0498 | YES | 464.8
31 | 0.6 | 175.89 | 105.534 | 15.3 | 6.29 | 19.5507 | YES | 466.2
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2