## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lane
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2023-08-01
System Name: | Rainbow Water District |  |  | ID#: 4100839 |  | WTP ID: TP- | Chase
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 107 |  | 4.5 | 25 | 0.017 | 0.019
2 | 107 |  | 4.5 | 25 | 0.019 | 0.018
3 | 107 |  | 4.5 | 25 | 0.017 | 0.018
4 | 106 |  | 4.6 | 25 | 0.019 | 0.021
5 | 103 |  | 4.6 | 25 | 0.017 | 0.017
6 | 105 |  | 4.8 | 25 | 0.019 | 0.019
7 | 107 |  | 4.8 | 25 | 0.019 | 0.019
8 | 107 |  | 4.9 | 25 | 0.017 | 0.017
9 | 107 |  | 4.8 | 25 | 0.018 | 0.018
10 | 107 |  | 4.9 | 25 | 0.017 | 0.017
11 | 106 |  | 4.8 | 25 | 0.017 | 0.017
12 | 109 |  | 4.8 | 25 | 0.018 | 0.018
13 | 105 |  | 4.9 | 25 | 0.017 | 0.017
14 | 106 |  | 4.9 | 25 | 0.019 | 0.019
15 | 107 |  | 4.9 | 25 | 0.017 | 0.017
16 | 106 |  | 5 | 25 | 0.017 | 0.017
17 | 106 |  | 4.9 | 25 | 0.017 | 0.017
18 | 107 |  | 4.9 | 25 | 0.017 | 0.017
19 | 107 |  | 4.9 | 25 | 0.018 | 0.018
20 | 107 |  | 5.1 | 25 | 0.018 | 0.018
21 | 108 |  | 5.1 | 25 | 0.019 | 0.019
22 | 108 |  | 5 | 25 | 0.018 | 0.018
23 | 110 |  | 5 | 25 | 0.02 | 0.02
24 | 110 |  | 5.3 | 25 | 0.02 | 0.02
25 | 110 |  | 5.2 | 25 | 0.018 | 0.018
26 | 110 |  | 5.2 | 25 | 0.018 | 0.018
27 | 110 |  | 5.3 | 25 | 0.018 | 0.018
28 | 110 |  | 5.7 | 25 | 0.018 | 0.018
29 | 110 |  | 5.8 | 25 | 0.018 | 0.018
30 | 110 |  | 5.6 | 25 | 0.018 | 0.018
31 | 111 |  | 5.6 | 25 | 0.018 | 0.018
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Brian A. Scott
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE: 9/6/23
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 541 )844-5851 |  | CERT #: T-08428
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Chase
System Name: | Rainbow Water District |  | ID#: 41 00839 |  | Month/Year: | 2023-06-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.6 | 175.66 | 105.396 | 15.6 | 6.41 | 10.0208 | YES | 466.8
2 | 0.6 | 177.79 | 106.674 | 15.6 | 6.4 | 9.9833 | YES | 461.2
3 | 0.6 | 174.65 | 104.79 | 15.72 | 6.4 | 9.9025 | YES | 469.5
4 | 0.6 | 175.89 | 105.534 | 15.8 | 6.32 | 9.5571 | YES | 466.2
5 | 0.6 | 176.34 | 105.804 | 15.7 | 6.35 | 9.7313 | YES | 465
6 | 0.59 | 175.77 | 103.7043 | 15.9 | 6.42 | 9.845 | YES | 466.5
7 | 0.46 | 176.42 | 81.1532 | 16 | 6.43 | 9.669 | YES | 464.8
8 | 0.55 | 175.89 | 96.7395 | 15.9 | 6.39 | 9.6897 | YES | 466.2
9 | 0.56 | 175.89 | 98.4984 | 15.9 | 6.33 | 9.4843 | YES | 466.2
10 | 0.56 | 176.41 | 98.7896 | 16 | 6.43 | 9.7815 | YES | 464.8
11 | 0.57 | 176.34 | 100.5138 | 16.04 | 6.31 | 9.335 | YES | 465
12 | 0.56 | 176.26 | 98.7056 | 16 | 6.4 | 9.6717 | YES | 465.2
13 | 0.55 | 177.02 | 97.361 | 16 | 6.3 | 9.3035 | YES | 463.2
14 | 0.54 | 176.34 | 95.2236 | 16.1 | 6.34 | 9.3701 | YES | 465
15 | 0.53 | 176.64 | 93.6192 | 16.1 | 6.25 | 9.047 | YES | 464.2
16 | 0.52 | 174.65 | 90.818 | 16.2 | 6.29 | 9.1118 | YES | 469.5
17 | 0.53 | 175.66 | 93.0998 | 16.2 | 6.31 | 9.1914 | YES | 466.8
18 | 0.52 | 176.26 | 91.6552 | 16.2 | 6.3 | 9.1462 | YES | 465.2
19 | 0.52 | 175.96 | 91.4992 | 16.2 | 6.39 | 9.4617 | YES | 466
20 | 0.53 | 179.64 | 95.2092 | 16.2 | 6.3 | 9.1568 | YES | 464.2
21 | 0.52 | 176.26 | 91.6552 | 16.3 | 6.42 | 9.5046 | YES | 465.2
22 | 0.54 | 176.53 | 95.3262 | 16.3 | 6.39 | 9.4196 | YES | 464.5
23 | 0.53 | 175.77 | 93.1581 | 16.3 | 6.44 | 9.5875 | YES | 466.5
24 | 0.56 | 175.4 | 98.224 | 16.1 | 6.88 | 11.5011 | YES | 467.5
25 | 0.54 | 174.65 | 94.311 | 16.2 | 6.94 | 11.6562 | YES | 469.5
26 | 0.54 | 177.18 | 95.6772 | 16.9 | 6.89 | 10.9134 | YES | 462.8
27 | 0.53 | 173.36 | 91.8808 | 16.9 | 6.69 | 10.1131 | YES | 473
28 | 0.55 | 175.66 | 96.613 | 17 | 6.89 | 10.8526 | YES | 466.8
29 | 0.55 | 175.02 | 96.261 | 16 | 6.93 | 11.7836 | YES | 468.5
30 | 0.54 | 175.58 | 94.8132 | 16 | 6.94 | 11.8141 | YES | 467
31 | 0.54 | 176.22 | 95.1588 | 16.8 | 6.82 | 10.7029 | YES | 464
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised August 2023
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2