## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lane
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2023-10-01
System Name: | Rainbow Water District |  |  | ID#: 4100839 |  | WTP ID: TP- | Chase
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | Offline |  | Offline | 25
2 | Offline |  | Offline | 25
3 | Offline |  | Offline | 25
4 | Offline |  | Offline | 25
5 | Offline |  | Offline | 25
6 | 107 |  | 5.7 | 25 | 0.018 | 0.074
7 | 109 |  | 6 | 25 | 0.011 | 0.012
8 | 110 |  | 6.2 | 25 | 0.011 | 0.012
9 | 112 |  | 6.3 | 25 | 0.011 | 0.014
10 | 114 |  | 6.3 | 25 | 0.017 | 0.017
11 | 114 |  | 6.5 | 25 | 0.017 | 0.02
12 | 114 |  | 6.6 | 25 | 0.017 | 0.026
13 | 114 |  | 7.5 | 25 | 0.017 | 0.02
14 | 114 |  | 7.5 | 25 | 0.019 | 0.02
15 | 118 |  | 7.5 | 25 | 0.015 | 0.015
16 | 116 |  | 7.9 | 25 | 0.019 | 0.019
17 | 118 |  | 7.9 | 25 | 0.015 | 0.02
18 | 120 |  | 8.1 | 25 | 0.015 | 0.02
19 | 120 |  | 8.1 | 25 | 0.014 | 0.021
20 | 120 |  | 8.5 | 25 | 0.012 | 0.015
21 | 121 |  | 8.4 | 25 | 0.012 | 0.013
22 | 123 |  | 8.6 | 25 | 0.014 | 0.014
23 | 127 |  | 8.7 | 25 | 0.015 | 0.018
24 | 122 |  | 7.5 | 25 | 0.015 | 0.019
25 | 126 |  | 8.1 | 25 | 0.015 | 0.015
26 | 129 |  | 8.5 | 25 | 0.012 | 0.015
27 | 131 |  | 7.6 | 25 | 0.015 | 0.017
28 | 132 |  | 7.9 | 25 | 0.012 | 0.013
29 | 135 |  | 7.9 | 25 | 0.02 | 0.02
30 | 108 |  | 7.6 | 25 | 0.02 | 0.026
31 | 108 |  | 8 | 25 | 0.015 | 0.02
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: ERIC CARLSON
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE: 11/7/23
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 541 ) 954-9941 |  | CERT #: T-09011
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Chase
System Name: | Rainbow Water District |  | ID#: 4100839 |  | Month/Year: | 2023-10-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | Offline |  | #VALUE! |  |  | #VALUE! | #VALUE!
2 | Offline |  | #VALUE! |  |  | #VALUE! | #VALUE!
3 | Offline |  | #VALUE! |  |  | #VALUE! | #VALUE!
4 | Offline |  | #VALUE! |  |  | #VALUE! | #VALUE!
5 | Offline |  | #VALUE! |  |  | #VALUE! | #VALUE!
6 | 0.45 | 175.66 | 79.047 | 16.4 | 7.34 | 26.4272 | YES | 466.8
7 | 0.6 | 176.72 | 106.032 | 16.4 | 7.39 | 27.3892 | YES | 464
8 | 0.61 | 176.15 | 107.4515 | 16.2 | 7.35 | 27.3799 | YES | 465.5
9 | 0.57 | 176.91 | 100.8387 | 16 | 7.35 | 27.6222 | YES | 463.5
10 | 0.56 | 174.91 | 97.9496 | 16.1 | 6.96 | 23.7002 | YES | 468.8
11 | 0.57 | 176.72 | 100.7304 | 15.2 | 6.96 | 25.206 | YES | 464
12 | 0.58 | 176.72 | 102.4976 | 15.2 | 6.94 | 25.0475 | YES | 464
13 | 0.56 | 177.87 | 99.6072 | 16.1 | 6.89 | 23.0884 | YES | 461
14 | 0.56 | 177.02 | 99.1312 | 15.9 | 6.83 | 22.8823 | YES | 463.2
15 | 0.56 | 177.56 | 99.4336 | 16 | 6.94 | 23.6825 | YES | 461.8
16 | 0.56 | 176.15 | 98.644 | 15.8 | 6.91 | 23.7358 | YES | 465.5
17 | 0.56 | 177.41 | 99.3496 | 15.9 | 6.84 | 22.968 | YES | 462.2
18 | 0.56 | 175.28 | 98.1568 | 16 | 6.88 | 23.1576 | YES | 467.8
19 | 0.57 | 176.64 | 100.6848 | 15.85 | 6.88 | 23.4194 | YES | 464.2
20 | 0.57 | 176.53 | 100.6221 | 15.85 | 6.91 | 23.6833 | YES | 464.5
21 | 0.56 | 176.72 | 98.9632 | 15.76 | 6.9 | 23.711 | YES | 464
22 | 0.55 | 176.72 | 97.196 | 15.78 | 6.91 | 23.7404 | YES | 464
23 | 0.45 | 176.72 | 79.524 | 15.7 | 6.92 | 23.6843 | YES | 464
24 | 0.53 | 177.79 | 94.2287 | 15.7 | 6.86 | 23.3731 | YES | 461.2
25 | 0.53 | 177.56 | 94.1068 | 15.7 | 6.9 | 23.725 | YES | 461.8
26 | 0.58 | 176.8 | 102.544 | 15.7 | 6.93 | 24.1303 | YES | 463.8
27 | 0.39 | 178.26 | 69.5214 | 15.8 | 6.94 | 23.5392 | YES | 460
28 | 0.47 | 199.75 | 93.8825 | 15.6 | 6.92 | 23.8988 | YES | 410.5
29 | 0.48 | 175.96 | 84.4608 | 15.5 | 6.84 | 23.3787 | YES | 411.2
30 | 0.37 | 175.96 | 65.1052 | 15.4 | 6.91 | 23.8566 | YES | 466
31 | 0.64 | 176.26 | 112.8064 | 15.5 | 6.93 | 24.6256 | YES | 465.2
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2