## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lane
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-04-01
System Name: | Rainbow Water District |  |  | ID#: 4100839 |  | WTP ID: TP- | Chase
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 115 |  | 14.3 | 25 | 0.019 | 0.021
2 | 114 |  | 14.2 | 25 | 0.02 | 0.02
3 | 115 |  | 14 | 25 | 0.02 | 0.02
4 | 116 |  | 14.1 | 25 | 0.019 | 0.02
5 | 116 |  | 14.4 | 25 | 0.019 | 0.02
6 | 113 |  | 13.6 | 25 | 0.02 | 0.02
7 | 114 |  | 13.7 | 25 | 0.02 | 0.02
8 | 114 |  | 13.4 | 25 | 0.02 | 0.02
9 | 115 |  | 13.8 | 25 | 0.019 | 0.02
10 | 114 |  | 13.7 | 25 | 0.02 | 0.02
11 | 115 |  | 13.5 | 25 | 0.019 | 0.019
12 | 116 |  | 13.8 | 25 | 0.02 | 0.02
13 | 119 |  | 13.7 | 25 | 0.019 | 0.02
14 | 114 |  | 13.6 | 25 | 0.02 | 0.02
15 | 115 |  | 13.7 | 25 | 0.02 | 0.02
16 | 116 |  | 14.1 | 25 | 0.02 | 0.02
17 | 116 |  | 13.5 | 25 | 0.019 | 0.02
18 | 114 |  | 13.5 | 25 | 0.02 | 0.02
19 | 116 |  | 13.5 | 25 | 0.017 | 0.018
20 | 121 |  | 18 | 25 | 0.017 | 0.02
21 | 120 |  | 17.9 | 25 | 0.017 | 0.02
22 | 120 |  | 18.5 | 25 | 0.019 | 0.02
23 | 122 |  | 18.5 | 25 | 0.017 | 0.023
24 | 115 |  | 12.9 | 25 | 0.019 | 0.02
25 | 114 |  | 13.6 | 25 | 0.019 | 0.02
26 | 114 |  | 12.8 | 25 | 0.02 | 0.026
27 | 115 |  | 13.5 | 25 | 0.02 | 0.02
28 | 114 |  | 13.5 | 25 | 0.02 | 0.02
29 | 116 |  | 14.1 | 25 | 0.02 | 0.02
30 | 116 |  | 13.7 | 25 | 0.017 | 0.018
31
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Eric Carlson
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE: 5/3/24
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 541 ) 954-9941 |  | CERT #:T-09011
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Chase
System Name: | Rainbow Water District |  | ID#: 4100839 |  | Month/Year: | 2024-04-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.68 | 185.73 | 126.2964 | 12.2 | 6.57 | 28.0181 | YES | 441.5
2 | 0.68 | 185.01 | 125.8068 | 12.2 | 6.58 | 28.1108 | YES | 443.2
3 | 0.7 | 184.89 | 129.423 | 12.4 | 6.53 | 27.3693 | YES | 443.5
4 | 0.7 | 186.78 | 130.746 | 12.3 | 6.64 | 28.5575 | YES | 439
5 | 0.68 | 185.73 | 126.2964 | 12.2 | 6.59 | 28.2038 | YES | 441.5
6 | 0.69 | 184.35 | 127.2015 | 12.2 | 6.55 | 27.8633 | YES | 444.8
7 | 0.69 | 186.15 | 128.4435 | 12.2 | 6.53 | 27.6802 | YES | 440.5
8 | 0.64 | 158.44 | 101.4016 | 12.3 | 6.57 | 27.7274 | YES | 442.2
9 | 0.58 | 185.94 | 107.8452 | 12.4 | 6.54 | 27.1138 | YES | 441
10 | 0.55 | 185.86 | 102.223 | 12.3 | 6.56 | 27.3744 | YES | 441.2
11 | 0.57 | 185.73 | 105.8661 | 12.1 | 6.58 | 27.9573 | YES | 441.5
12 | 0.57 | 189.59 | 108.0663 | 12.2 | 6.57 | 27.6933 | YES | 438.5
13 | 0.58 | 186.57 | 108.2106 | 12 | 6.53 | 27.7001 | YES | 439.5
14 | 0.46 | 186.7 | 85.882 | 12.2 | 6.56 | 27.2832 | YES | 439.2
15 | 0.57 | 186.44 | 106.2708 | 12.1 | 6.56 | 27.7734 | YES | 439.8
16 | 0.59 | 187.12 | 110.4008 | 12.1 | 6.61 | 28.2958 | YES | 438.2
17 | 0.59 | 186.7 | 110.153 | 12.3 | 6.54 | 27.3102 | YES | 439.2
18 | 0.6 | 185.73 | 111.438 | 12.5 | 6.5 | 25.5405 | YES | 441.5
19 | 0.56 | 185.73 | 104.0088 | 12.5 | 6.58 | 26.1926 | YES | 441.5
20 | 0.62 | 186.78 | 115.8036 | 12.5 | 6.58 | 26.3731 | YES | 439
21 | 0.62 | 187.21 | 116.0702 | 12.7 | 6.6 | 26.2164 | YES | 438
22 | 0.59 | 187.21 | 110.4539 | 12.5 | 6.52 | 25.702 | YES | 438
23 | 0.59 | 186.36 | 109.9524 | 12.6 | 6.6 | 26.3022 | YES | 440
24 | 0.61 | 182.7 | 111.447 | 12.6 | 6.52 | 25.5888 | YES | 448.8
25 | 0.6 | 185.85 | 111.51 | 12.5 | 6.58 | 26.3128 | YES | 441.2
26 | 0.6 | 186.44 | 111.864 | 12.6 | 6.53 | 25.6549 | YES | 439.8
27 | 0.63 | 186.78 | 117.6714 | 12.4 | 6.53 | 27.1678 | YES | 439
28 | 0.63 | 184.06 | 115.9578 | 12.6 | 6.52 | 25.6474 | YES | 445.5
29 | 0.64 | 185.73 | 118.8672 | 12.6 | 6.55 | 25.9653 | YES | 441.5
30 | 0.64 | 184.68 | 118.1952 | 12.8 | 6.57 | 25.811 | YES | 444
31
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2