## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lane
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-07-01
System Name: | Rainbow Water District |  |  | ID#: 4100839 |  | WTP ID: TP- | Chase
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 103 |  | 1 | 25 | 0.019 | 0.019
2 | 102 |  | 1.1 | 25 | 0.019 | 0.022
3 | 102 |  | 1.1 | 25 | 0.019 | 0.019
4 | 102 |  | 1 | 25 | 0.018 | 0.018
5 | 101 |  | 1 | 25 | 0.019 | 0.019
6 | 102 |  | 1 | 25 | 0.019 | 0.019
7 | 104 |  | 1.2 | 25 | 0.019 | 0.019
8 | 102 |  | 1.1 | 25 | 0.019 | 0.019
9 | 102 |  | 1.3 | 25 | 0.019 | 0.019
10 | 102 |  | 1.2 | 25 | 0.019 | 0.019
11 | 103 |  | 1.2 | 25 | 0.019 | 0.019
12 | 102 |  | 1.2 | 25 | 0.04 | 0.04
13 | 103 |  | 1.25 | 25 | 0.017 | 0.018
14 | 103 |  | 1.26 | 25 | 0.019 | 0.019
15 | 103 |  | 1.28 | 25 | 0.019 | 0.019
16 | 103 |  | 1.27 | 25 | 0.019 | 0.019
17 | 103 |  | 1.3 | 25 | 0.019 | 0.02
18 | 103 |  | 1.27 | 25 | 0.019 | 0.019
19 | 103 |  | 1.3 | 25 | 0.019 | 0.019
20 | 102 |  | 1.2 | 25 | 0.019 | 0.019
21 | 104 |  | 1.3 | 25 | 0.017 | 0.018
22 | 103 |  | 1.4 | 25 | 0.019 | 0.019
23 | 104 |  | 1.3 | 25 | 0.019 | 0.02
24 | 103 |  | 1.4 | 25 | 0.019 | 0.019
25 | 103 |  | 1.4 | 25 | 0.019 | 0.019
26 | 103 |  | 1.4 | 25 | 0.019 | 0.019
27 | 103 |  | 1.4 | 25 | 0.018 | 0.018
28 | 104 |  | 1.4 | 25 | 0.019 | 0.019
29 | 103 |  | 1.5 | 25 | 0.019 | 0.02
30 | 104 |  | 1.4 | 25 | 0.017 | 0.018
31 | 104 |  | 1.6 | 25 | 0.017 | 0.019
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Eric Carlson
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE:8/8/24
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 541 ) 954-9941 |  | CERT #: T-09011
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Chase
System Name: | Rainbow Water District |  | ID#: 4100839 |  | Month/Year: | 2024-07-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.57 | 184.68 | 105.2676 | 14.15 | 6.7 | 24.5481 | YES | 444
2 | 0.57 | 183.24 | 104.4468 | 14.08 | 6.6 | 23.7603 | YES | 447.5
3 | 0.45 | 185.01 | 83.2545 | 14.3 | 6.69 | 23.8803 | YES | 443.2
4 | 0.56 | 186.27 | 104.3112 | 14.3 | 6.68 | 24.0936 | YES | 440.2
5 | 0.55 | 184.26 | 101.343 | 14.4 | 6.62 | 23.3751 | YES | 445
6 | 0.55 | 184.26 | 101.343 | 14.5 | 6.64 | 23.3925 | YES | 445
7 | 0.54 | 185.94 | 100.4076 | 14.9 | 6.74 | 23.6111 | YES | 441
8 | 0.55 | 184.76 | 101.618 | 14.8 | 6.68 | 23.2703 | YES | 443.8
9 | 0.54 | 185.31 | 100.0674 | 14.95 | 6.68 | 23.0101 | YES | 442.2
10 | 0.53 | 183.85 | 97.4405 | 15.2 | 6.66 | 22.4316 | YES | 446
11 | 0.55 | 183.93 | 101.1615 | 15.1 | 6.67 | 22.7201 | YES | 445.8
12 | 0.6 | 183.77 | 110.262 | 15.63 | 6.68 | 22.1323 | YES | 446.2
13 | 0.6 | 183.52 | 110.112 | 15.4 | 6.72 | 22.8167 | YES | 446.8
14 | 0.57 | 183.65 | 104.6805 | 15.3 | 6.67 | 22.4677 | YES | 446.5
15 | 0.58 | 183.11 | 106.2038 | 15.6 | 6.72 | 22.4598 | YES | 447.8
16 | 0.56 | 182.95 | 102.452 | 15.6 | 6.71 | 22.3245 | YES | 448.2
17 | 0.58 | 181.01 | 104.9858 | 15.5 | 6.67 | 22.1925 | YES | 453
18 | 0.59 | 185.1 | 109.209 | 15.5 | 6.6 | 21.6433 | YES | 443
19 | 0.58 | 182.83 | 106.0414 | 15.8 | 6.71 | 22.0764 | YES | 448.5
20 | 0.57 | 183.03 | 104.3271 | 15.8 | 6.7 | 21.9686 | YES | 448
21 | 0.59 | 184.68 | 108.9612 | 15.9 | 6.65 | 21.4654 | YES | 444
22 | 0.58 | 184.06 | 106.7548 | 15.9 | 6.67 | 21.602 | YES | 445.5
23 | 0.58 | 183.44 | 106.3952 | 16.1 | 6.69 | 21.4728 | YES | 447
24 | 0.57 | 183.77 | 104.7489 | 16 | 6.67 | 21.432 | YES | 446.2
25 | 0.57 | 185.6 | 105.792 | 16.1 | 6.62 | 20.8925 | YES | 441.8
26 | 0.56 | 183.36 | 102.6816 | 16.2 | 6.73 | 21.6006 | YES | 447.2
27 | 0.57 | 181.09 | 103.2213 | 16.1 | 6.61 | 20.8142 | YES | 452.8
28 | 0.57 | 184.6 | 105.222 | 16.1 | 6.45 | 19.6003 | YES | 444.2
29 | 0.58 | 183.85 | 106.633 | 16.2 | 6.56 | 20.3131 | YES | 446
30 | 0.57 | 184.18 | 104.9826 | 16.2 | 6.67 | 21.1447 | YES | 445.2
31 | 0.55 | 182.54 | 100.397 | 16.4 | 6.74 | 21.3665 | YES | 449.2
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2