## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lane
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-08-01
System Name: | Rainbow Water District |  |  | ID#: 4100839 |  | WTP ID: TP- | Chase
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 105 |  | 1.7 | 25 | 0.016 | 0.018
2 | 104 |  | 1.5 | 25 | 0.017 | 0.019
3 | 104 |  | 1.6 | 25 | 0.02 | 0.02
4 | 103 |  | 1.6 | 25 | 0.02 | 0.018
5 | 104 |  | 1.7 | 25 | 0.017 | 0.019
6 | 104 |  | 1.6 | 25 | 0.02 | 0.021
7 | 104 |  | 1.5 | 25 | 0.02 | 0.02
8 | 104 |  | 1.6 | 25 | 0.019 | 0.025
9 | 104 |  | 1.7 | 25 | 0.019 | 0.019
10 | 104 |  | 1.6 | 25 | 0.018 | 0.018
11 | 104 |  | 1.7 | 25 | 0.018 | 0.02
12 | 105 |  | 1.7 | 25 | 0.02 | 0.026
13 | 106 |  | 1.8 | 25 | 0.025 | 0.026
14 | 104 |  | 1.8 | 25 | 0.02 | 0.021
15 | 105 |  | 1.9 | 25 | 0.02 | 0.024
16 | 105 |  | 1.9 | 25 | 0.019 | 0.019
17 | 106 |  | 1.9 | 25 | 0.02 | 0.02
18 | 105 |  | 1.9 | 25 | 0.02 | 0.026
19 | 107 |  | 2 | 25 | 0.019 | 0.019
20 | 107 |  | 2.1 | 25 | 0.019 | 0.019
21 | 107 |  | 2.1 | 25 | 0.019 | 0.019
22 | 107 |  | 2 | 25 | 0.0019 | 0.02
23 | 108 |  | 2 | 25 | 0.019 | 0.019
24 | 108 |  | 2.2 | 25 | 0.019 | 0.019
25 | 108 |  | 2.2 | 25 | 0.019 | 0.019
26 | 108 |  | 2.1 | 25 | 0.019 | 0.019
27 | 108 |  | 2.2 | 25 | 0.019 | 0.019
28 | 108 |  | 2.1 | 25 | 0.019 | 0.02
29 | 108 |  | 2.2 | 25 | 0.019 | 0.035
30 | 109 |  | 2.2 | 25 | 0.019 | 0.024
31 | 108 |  | 2.2 | 25 | 0.018 | 0.019
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Eric Carlson
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE: 9/6/24
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 541 ) 954-9941 |  | CERT #: T-09011
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Chase
System Name: | Rainbow Water District |  | ID#: 4100839 |  | Month/Year: | 2024-08-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.54 | 184.68 | 99.7272 | 16.6 | 6.74 | 21.0557 | YES | 444
2 | 0.55 | 184.18 | 101.299 | 16.5 | 6.63 | 20.3647 | YES | 445.2
3 | 0.54 | 184.18 | 99.4572 | 16.4 | 6.41 | 18.8533 | YES | 445.2
4 | 0.54 | 183.44 | 99.0576 | 16.5 | 6.69 | 20.8045 | YES | 447
5 | 0.54 | 184.06 | 99.3924 | 16.5 | 6.73 | 21.119 | YES | 445.5
6 | 0.53 | 185.43 | 98.2779 | 16.8 | 6.65 | 20.0598 | YES | 442.2
7 | 0.55 | 184.89 | 101.6895 | 16.4 | 6.65 | 20.6573 | YES | 443.5
8 | 0.54 | 185.52 | 100.1808 | 16.5 | 6.65 | 20.4946 | YES | 442
9 | 0.54 | 183.85 | 99.279 | 16.6 | 6.62 | 20.1284 | YES | 446
10 | 0.54 | 185.01 | 99.9054 | 16.5 | 6.49 | 19.2985 | YES | 443.2
11 | 0.54 | 184.6 | 99.684 | 16.6 | 6.52 | 19.3858 | YES | 444.2
12 | 0.54 | 185.52 | 100.1808 | 16.9 | 6.58 | 19.4295 | YES | 442
13 | 0.56 | 185.85 | 104.076 | 16.8 | 6.7 | 20.511 | YES | 441.2
14 | 0.48 | 184.18 | 88.4064 | 17 | 6.72 | 20.2006 | YES | 445.2
15 | 0.49 | 185.73 | 91.0077 | 17.2 | 6.74 | 20.1027 | YES | 441.5
16 | 0.49 | 180.28 | 88.3372 | 16.9 | 6.69 | 20.133 | YES | 454.8
17 | 0.5 | 186.15 | 93.075 | 16.9 | 6.53 | 18.9792 | YES | 440.5
18 | 0.51 | 186.7 | 95.217 | 16.9 | 6.71 | 20.3317 | YES | 439.2
19 | 0.5 | 184.76 | 92.38 | 17 | 6.67 | 19.8705 | YES | 443.8
20 | 0.5 | 182.54 | 91.27 | 16.9 | 6.68 | 20.0807 | YES | 449.2
21 | 0.5 | 185.73 | 92.865 | 16.9 | 6.67 | 20.0054 | YES | 441.5
22 | 0.5 | 184.35 | 92.175 | 16.8 | 6.48 | 18.7519 | YES | 444.8
23 | 0.57 | 181.21 | 103.2897 | 16.8 | 6.68 | 20.3811 | YES | 452.5
24 | 0.53 | 185.18 | 98.1454 | 16.7 | 6.65 | 20.196 | YES | 442.8
25 | 0.51 | 183.52 | 93.5952 | 16.8 | 6.69 | 20.3165 | YES | 446.8
26 | 0.49 | 185.01 | 90.6549 | 16.7 | 6.85 | 21.6691 | YES | 443.2
27 | 0.51 | 185.52 | 94.6152 | 16.5 | 6.88 | 22.2625 | YES | 442
28 | 0.5 | 185.31 | 92.655 | 16.4 | 6.89 | 22.4712 | YES | 442.5
29 | 0.49 | 186.36 | 91.3164 | 16.6 | 6.92 | 22.3949 | YES | 440
30 | 0.46 | 185.52 | 85.3392 | 16.5 | 6.65 | 20.3061 | YES | 442
31 | 0.47 | 186.36 | 87.5892 | 16.6 | 6.83 | 21.6031 | YES | 440
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2