## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lane
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-09-01
System Name: | Rainbow Water District |  |  | ID#: 4100839 |  | WTP ID: TP- | Chase
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 108 |  | 2.3 | 25 | 0.018 | 0.018
2 | 109 |  | 2.2 | 25 | 0.019 | 0.02
3 | 109 |  | 2.2 | 25 | 0.019 | 0.033
4 | 109 |  | 2.2 | 25 | 0.019 | 0.019
5 | 110 |  | 2.3 | 25 | 0.019 | 0.019
6 | 110 |  | 2.4 | 25 | 0.019 | 0.019
7 | 111 |  | 2.4 | 25 | 0.019 | 0.019
8 | 110 |  | 2.4 | 25 | 0.019 | 0.019
9 | 111 |  | 2.4 | 25 | 0.019 | 0.019
10 | 111 |  | 2.3 | 25 | 0.018 | 0.018
11 | 112 |  | 2.5 | 25 | 0.017 | 0.026
12 | 107 |  | 1.9 | 25 | 0.026 | 0.026
13 | 108 |  | 2.2 | 25 | 0.024 | 0.024
14 | 110 |  | 2.4 | 25 | 0.017 | 0.018
15 | 111 |  | 2.3 | 25 | 0.017 | 0.02
16 | 113 |  | 2.4 | 25 | 0.017 | 0.02
17 | 113 |  | 2.5 | 25 | 0.017 | 0.02
18 | 113 |  | 2.3 | 25 | 0.017 | 0.02
19 | 113 |  | 2.4 | 25 | 0.017 | 0.02
20 | 114 |  | 2.4 | 25 | 0.019 | 0.02
21 | 112 |  | 2.4 | 25 | 0.019 | 0.02
22 | 112 |  | 2.5 | 25 | 0.019 | 0.02
23 | 115 |  | 2.5 | 25 | 0.019 | 0.019
24 | 113 |  | 2.4 | 25 | 0.017 | 0.018
25 | 115 |  | 2.3 | 25 | 0.017 | 0.02
26 | 117 |  | 2.6 | 25 | 0.02 | 0.02
27 | 115 |  | 2.5 | 25 | 0.019 | 0.02
28 | 115 |  | 2.4 | 25 | 0.013 | 0.02
29 | 117 |  | 2.5 | 25 | 0.017 | 0.02
30 | 116 |  | 2.5 | 25 | 0.02 | 0.02
31
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Eric Carlson
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE: 10/8/24
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 541 ) 541-954-9941 |  | CERT #:T-09011
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Chase
System Name: | Rainbow Water District |  | ID#: 4100839 |  | Month/Year: | 2024-09-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.49 | 184.76 | 90.5324 | 16.4 | 6.68 | 20.7471 | YES | 443.8
2 | 0.49 | 185.31 | 90.8019 | 16.4 | 6.68 | 20.7471 | YES | 442.5
3 | 0.53 | 183.36 | 97.1808 | 16.6 | 6.93 | 22.5825 | YES | 447.2
4 | 0.49 | 185.85 | 91.0665 | 16.5 | 6.93 | 22.6308 | YES | 441.2
5 | 0.45 | 184.26 | 82.917 | 16.7 | 6.97 | 22.5605 | YES | 445
6 | 0.48 | 184.68 | 88.6464 | 16.5 | 6.73 | 20.9734 | YES | 444
7 | 0.47 | 185.1 | 86.997 | 16.5 | 6.68 | 20.5599 | YES | 443
8 | 0.48 | 185.18 | 88.8864 | 16.4 | 6.69 | 20.8011 | YES | 442.8
9 | 0.47 | 184.68 | 86.7996 | 16.6 | 6.97 | 22.7653 | YES | 444
10 | 0.47 | 184.6 | 86.762 | 16.3 | 6.65 | 20.6063 | YES | 444.2
11 | 0.49 | 185.6 | 90.944 | 16.3 | 6.7 | 21.045 | YES | 441.8
12 | 0.43 | 281.01 | 120.8343 | 16.2 | 6.91 | 22.7629 | YES | 291.8
13 | 0.67 | 184.76 | 123.7892 | 16.7 | 7.04 | 23.7515 | YES | 443.8
14 | 0.64 | 184.6 | 118.144 | 16.2 | 6.91 | 23.319 | YES | 444.2
15 | 0.63 | 185.6 | 116.928 | 16.2 | 6.84 | 22.6906 | YES | 441.8
16 | 0.63 | 185.73 | 117.0099 | 16.1 | 6.91 | 23.4495 | YES | 441.5
17 | 0.63 | 185.43 | 116.8209 | 16 | 6.91 | 23.6077 | YES | 442.2
18 | 0.63 | 185.43 | 116.8209 | 16 | 6.95 | 23.9629 | YES | 442.2
19 | 0.62 | 185.73 | 115.1526 | 16 | 6.91 | 23.5806 | YES | 441.5
20 | 0.63 | 186.87 | 117.7281 | 15.9 | 6.89 | 23.5901 | YES | 438.8
21 | 0.64 | 186.27 | 119.2128 | 15.7 | 6.86 | 23.6703 | YES | 440.2
22 | 0.63 | 186.44 | 117.4572 | 15.7 | 6.86 | 23.6431 | YES | 439.8
23 | 0.62 | 210.14 | 130.2868 | 15.7 | 6.91 | 24.061 | YES | 390.2
24 | 0.58 | 185.52 | 107.6016 | 15.8 | 6.88 | 23.5253 | YES | 442
25 | 0.59 | 184.89 | 109.0851 | 15.7 | 6.89 | 23.7999 | YES | 443.5
26 | 0.64 | 185.43 | 118.6752 | 15.6 | 6.9 | 24.1885 | YES | 442.2
27 | 0.48 | 185.85 | 89.208 | 15.6 | 6.88 | 23.5716 | YES | 441.2
28 | 0.6 | 185.85 | 111.51 | 15.5 | 6.8 | 23.3516 | YES | 441.2
29 | 0.61 | 185.56 | 113.1916 | 15.7 | 6.95 | 24.3948 | YES | 441.8
30 | 0.62 | 186.02 | 115.3324 | 15.5 | 6.92 | 24.4777 | YES | 440.8
31
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2