## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lane
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-10-01
System Name: | Rainbow Water District |  |  | ID#: 4100839 |  | WTP ID: TP- | Chase
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 110 |  | 2.5 | 25 | 0.017 | 0.02
2 | 119 |  | 2.4 | 25 | 0.017 | 0.02
3 | 120 |  | 2.5 | 25 | 0.017 | 0.02
4 | 120 |  | 2.5 | 25 | 0.017 | 0.026
5 | 116 |  | 3.4 | 25 | 0.017 | 0.02
6 | 118 |  | 3.2 | 25 | 0.017 | 0.02
7 | 118 |  | 3.2 | 25 | 0.02 | 0.087
8 | 109 |  | 3.2 | 25 | 0.025 | 0.033
9 | 110 |  | 3.4 | 25 | 0.019 | 0.02
10 | 109 |  | 3.4 | 25 | 0.02 | 0.026
11 | 110 |  | 3.6 | 25 | 0.02 | 0.02
12 | 109 |  | 3.3 | 25 | 0.02 | 0.02
13 | 109 |  | 3.3 | 25 | 0.02 | 0.02
14 | 111 |  | 3.4 | 25 | 0.017 | 0.02
15 | 112 |  | 3.3 | 25 | 0.022 | 0.026
16 | 115 |  | 3.3 | 25 | 0.017 | 0.026
17 | 114 |  | 3.3 | 25 | 0.018 | 0.02
18 | 116 |  | 3.2 | 25 | 0.017 | 0.02
19 | 116 |  | 3.3 | 25 | 0.019 | 0.02
20 | 118 |  | 3.2 | 25 | 0.017 | 0.02
21 | 118 |  | 3.3 | 25 | 0.017 | 0.02
22 | 119 |  | 3.2 | 25 | 0.017 | 0.02
23 | 121 |  | 3.3 | 25 | 0.017 | 0.02
24 | 121 |  | 3.4 | 25 | 0.02 | 0.02
25 | Offline |  | Offline | 25 | Offline | Offline
26 | Offline |  | Offline | 25 | Offline | Offline
27 | Offline |  | Offline | 25 | Offline | Offline
28 | Offline |  | Offline | 25 | Offline | Offline
29 | Offline |  | Offline | 25 | Offline | Offline
30 | Offline |  | Offline | 25 | Offline | Offline
31 | Offline |  | Offline | 25 | Offline | Offline
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Eric Carlson
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE:11/4/24
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 541 ) 746-1676 |  | CERT #:T-09011
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Chase
System Name: | Rainbow Water District |  | ID#: 4100839 |  | Month/Year: | 2024-10-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.61 | 185.73 | 113.2953 | 15.6 | 6.93 | 24.3767 | YES | 441.5
2 | 0.61 | 185.6 | 113.216 | 15.6 | 6.83 | 23.4834 | YES | 441.8
3 | 0.61 | 185.94 | 113.4234 | 15.6 | 6.96 | 24.651 | YES | 441
4 | 0.61 | 185.31 | 113.0391 | 15.6 | 6.96 | 24.651 | YES | 442.5
5 | 0.71 | 184.89 | 131.2719 | 15.6 | 6.92 | 24.5661 | YES | 443.5
6 | 0.67 | 186.44 | 124.9148 | 15.5 | 6.95 | 24.8954 | YES | 439.8
7 | 0.67 | 186.36 | 124.8612 | 15.4 | 6.93 | 24.8769 | YES | 44
8 | 0.6 | 185.31 | 111.186 | 15.6 | 6.95 | 24.5311 | YES | 442.5
9 | 0.66 | 178.84 | 118.0344 | 15.4 | 6.89 | 24.4804 | YES | 458.5
10 | 0.65 | 185.52 | 120.588 | 15.3 | 6.88 | 24.5255 | YES | 442
11 | 0.64 | 185.52 | 118.7328 | 15.3 | 6.9 | 24.6808 | YES | 442
12 | 0.67 | 184.06 | 123.3202 | 15.2 | 6.89 | 24.8399 | YES | 445.5
13 | 0.67 | 185.1 | 124.017 | 15.2 | 6.89 | 24.8399 | YES | 443
14 | 0.67 | 185.73 | 124.4391 | 15.3 | 6.92 | 24.9512 | YES | 441.5
15 | 0.67 | 186.36 | 124.8612 | 15.5 | 6.95 | 24.8954 | YES | 440
16 | 0.63 | 184.89 | 116.4807 | 15.3 | 6.94 | 25.023 | YES | 443.5
17 | 0.71 | 185.6 | 131.776 | 15.1 | 6.9 | 25.2159 | YES | 441.8
18 | 0.72 | 185.31 | 133.4232 | 15.2 | 6.93 | 25.3579 | YES | 442.5
19 | 0.71 | 185.94 | 132.0174 | 15.3 | 6.89 | 24.7871 | YES | 441
20 | 0.69 | 186.27 | 128.5263 | 15.3 | 6.94 | 25.1956 | YES | 440.2
21 | 0.71 | 186.7 | 132.557 | 15.2 | 6.88 | 24.8612 | YES | 439.2
22 | 0.74 | 186.36 | 137.9064 | 15.2 | 6.95 | 25.6062 | YES | 440
23 | 0.74 | 186.02 | 137.6548 | 15.2 | 6.96 | 25.7018 | YES | 440.8
24 | 0.73 | 185.31 | 135.2763 | 15 | 6.91 | 25.5389 | YES | 442.5
25 | Offline | Offline | #VALUE! | Offline | Offline | #VALUE! | #VALUE! | Offline
26 | Offline | Offline | #VALUE! | Offline | Offline | #VALUE! | #VALUE! | Offline
27 | Offline | Offline | #VALUE! | Offline | Offline | #VALUE! | #VALUE! | Offline
28 | Offline | Offline | #VALUE! | Offline | Offline | #VALUE! | #VALUE! | Offline
29 | Offline | Offline | #VALUE! | Offline | Offline | #VALUE! | #VALUE! | Offline
30 | Offline | Offline | #VALUE! | Offline | Offline | #VALUE! | #VALUE! | Offline
31 | Offline | Offline | #VALUE! | Offline | Offline | #VALUE! | #VALUE! | Offline
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2