## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lane
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-12-01
System Name: | Rainbow Water District |  |  | ID#: 4100839 |  | WTP ID: TP- | Chase
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | Offline |  | Offline | 25 | Offline | Offline
2 | Offline |  | Offline | 25 | Offline | Offline
3 | 92 |  | 2.9 | 25 | 0.046 | 0.019
4 | 94 |  | 3.2 | 25 | 0.026 | 0.033
5 | Offline |  | Offline | 25 | Offline | Offline
6 | Offline |  | Offline | 25 | Offline | Offline
7 | Offline |  | Offline | 25 | Offline | Offline
8 | Offline |  | Offline | 25 | Offline | Offline
9 | Offline |  | Offline | 25 | Offline | Offline
10 | 109 |  | 3.3 | 25 | 0.017 | 0.02
11 | 109 |  | 3.5 | 25 | 0.017 | 0.02
12 | 110 |  | 3.6 | 25 | 0.017 | 0.02
13 | 112 |  | 3.6 | 25 | 0.019 | 0.024
14 | Offline |  | Offline | 25 | Offline | Offline
15 | Offline |  | Offline | 25 | Offline | Offline
16 | 107 |  | 3.4 | 25 | 0.02 | 0.036
17 | 112 |  | 3.7 | 25 | 0.019 | 0.027
18 | 115 |  | 4.2 | 25 | 0.035 | 0.04
19 | 118 |  | 4.4 | 25 | 0.034 | 0.063
20 | 120 |  | 4.4 | 25 | 0.028 | 0.074
21 | 121 |  | 4.3 | 25 | 0.027 | 0.033
22 | 122 |  | 4.3 | 25 | 0.022 | 0.027
23 | 124 |  | 4.3 | 25 | 0.02 | 0.027
24 | 123 |  | 4.3 | 25 | 0.02 | 0.027
25 | 132 |  | 4.8 | 25 | 0.048 | 0.06
26 | 104 |  | 4.7 | 25 | 0.05 | 0.083
27 | 108 |  | 6.4 | 25 | 0.135 | 0.21
28 | 109 |  | 8.8 | 25 | 0.152 | 0.213
29 | Offline |  | Offline | 25 | Offline | Offline
30 | Offline |  | Offline | 25 | Offline | Offline
31 | 109 |  | 7.4 | 25 | 0.067 | 0.275
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Eric Carlson
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE: 1/2/25
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 541 ) 746-1676 |  | CERT #:T-09011
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Chase
System Name: | Rainbow Water District |  | ID#: 4100839 |  | Month/Year: | 2024-12-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | Offline | Offline | #VALUE! | Offline | Offline | #VALUE! | Offline | Offline
2 | Offline | Offline | #VALUE! | Offline | Offline | #VALUE! | Offline | Offline
3 | 0.5 | 170.83 | 85.415 | 13.7 | 6.84 | 26.4422 | YES | 480
4 | 0.49 | 189.94 | 93.0706 | 13.6 | 6.84 | 26.5895 | YES | 441
5 | Offline | Offline | #VALUE! | Offline | Offline | #VALUE! | Offline | Offline
6 | Offline | Offline | #VALUE! | Offline | Offline | #VALUE! | Offline | Offline
7 | Offline | Offline | #VALUE! | Offline | Offline | #VALUE! | Offline | Offline
8 | Offline | Offline | #VALUE! | Offline | Offline | #VALUE! | Offline | Offline
9 | Offline | Offline | #VALUE! | Offline | Offline | #VALUE! | Offline | Offline
10 | 0.63 | 185.85 | 117.0855 | 13.5 | 6.88 | 27.6077 | YES | 441.1
11 | 0.65 | 185.34 | 120.471 | 13.6 | 6.88 | 27.4864 | YES | 441
12 | 0.65 | 187.55 | 121.9075 | 13.7 | 6.83 | 26.8 | YES | 437.2
13 | 0.66 | 187.42 | 123.6972 | 13.8 | 6.85 | 26.8506 | YES | 437.5
14 | Offline | Offline | #VALUE! | Offline | Offline | #VALUE! | Offline | Offline
15 | Offline | Offline | #VALUE! | Offline | Offline | #VALUE! | Offline | Offline
16 | 0.48 | 184.76 | 88.6848 | 13.7 | 6.87 | 26.6779 | YES | 443.8
17 | 0.64 | 185.85 | 118.944 | 13.3 | 6.87 | 27.9078 | YES | 441.2
18 | 0.62 | 185.31 | 114.8922 | 13.2 | 6.86 | 27.927 | YES | 442.5
19 | 0.62 | 185.31 | 114.8922 | 13.5 | 6.82 | 26.9678 | YES | 442.5
20 | 0.47 | 186.57 | 87.6879 | 13.8 | 6.82 | 25.9814 | YES | 439.5
21 | 0.58 | 186.78 | 108.3324 | 13.7 | 6.81 | 26.3891 | YES | 439
22 | 0.6 | 186.12 | 111.672 | 13.9 | 6.84 | 26.3905 | YES | 438.2
23 | 0.6 | 186.7 | 112.02 | 13.8 | 6.81 | 26.2729 | YES | 439.2
24 | 0.6 | 185.31 | 111.186 | 13.9 | 6.8 | 26.0004 | YES | 442.5
25 | 0.57 | 187.42 | 106.8294 | 13.4 | 6.85 | 27.2971 | YES | 437.5
26 | 0.48 | 168.72 | 80.9856 | 13.3 | 6.89 | 27.6066 | YES | 486
27 | 0.54 | 167.96 | 90.6984 | 12.7 | 6.89 | 28.9345 | YES | 488.2
28 | 0.48 | 169 | 81.12 | 12.9 | 6.9 | 28.4608 | YES | 485.2
29 | Offline | Offline | #VALUE! | Offline | Offline | #VALUE! | Offline | Offline
30 | Offline | Offline | #VALUE! | Offline | Offline | #VALUE! | Offline | Offline
31 | 0.37 | 214.65 | 79.4205 | 13.8 | 6.83 | 25.7814 | YES | 382
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2