## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lane
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-01-01
System Name: | Rainbow Water District |  |  | ID#: 4100839 |  | WTP ID: TP- | Chase
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 109 |  | 8 | 25 | 0.02 | 0.031
2 | 110 |  | 8.3 | 25 | 0.027 | 0.034
3 | 108 |  | 7.7 | 25 | 0.032 | 0.057
4 | 109 |  | 8.1 | 25 | 0.04 | 0.041
5 | 108 |  | 8.3 | 25 | 0.047 | 0.055
6 | 110 |  | 9 | 25 | 0.049 | 0.055
7 | 112 |  | 9.6 | 25 | 0.034 | 0.041
8 | 110 |  | 9.6 | 25 | 0.027 | 0.029
9 | 111 |  | 9.1 | 25 | 0.019 | 0.021
10 | 111 |  | 10.3 | 25 | 0.02 | 0.02
11 | 110 |  | 9.4 | 25 | 0.02 | 0.02
12 | 110 |  | 9.4 | 25 | 0.019 | 0.02
13 | 110 |  | 9.5 | 25 | 0.019 | 0.026
14 | 108 |  | 9.2 | 25 | 0.017 | 0.021
15 | 111 |  | 9 | 25 | 0.02 | 0.021
16 | 112 |  | 9.3 | 25 | 0.02 | 0.021
17 | 111 |  | 9.4 | 25 | 0.02 | 0.021
18 | 108 |  | 9.7 | 25 | 0.017 | 0.021
19 | 109 |  | 9.7 | 25 | 0.017 | 0.02
20 | 111 |  | 9.8 | 25 | 0.017 | 0.023
21 | 112 |  | 9.9 | 25 | 0.017 | 0.021
22 | 112 |  | 9.5 | 25 | 0.02 | 0.02
23 | 110 |  | 9.8 | 25 | 0.02 | 0.021
24 | 112 |  | 9.9 | 25 | 0.017 | 0.02
25 | 111 |  | 9.6 | 25 | 0.02 | 0.02
26 | 110 |  | 9.2 | 25 | 0.02 | 0.02
27 | 111 |  | 9.5 | 25 | 0.017 | 0.02
28 | 112 |  | 9.4 | 25 | 0.019 | 0.02
29 | 112 |  | 9.8 | 25 | 0.019 | 0.02
30 | 111 |  | 9.4 | 25 | 0.02 | 0.02
31 | 111 |  | 9.6 | 25 | 0.02 | 0.02
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Eric Carlson
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE: 2/4/25
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 541 ) 746-1676 |  | CERT #:T-09011
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Chase
System Name: | Rainbow Water District |  | ID#: 4100839 |  | Month/Year: | 2025-01-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.55 | 168.3 | 92.565 | 13.5 | 6.78 | 26.3576 | YES | 487.2
2 | 0.56 | 168.44 | 94.3264 | 13.7 | 6.79 | 26.1335 | YES | 486.8
3 | 0.52 | 187.55 | 97.526 | 13.4 | 6.78 | 26.4438 | YES | 437.2
4 | 0.56 | 186.7 | 104.552 | 13.2 | 6.81 | 27.2255 | YES | 439.2
5 | 0.56 | 187 | 104.72 | 13.2 | 6.79 | 27.0237 | YES | 438.5
6 | 0.54 | 187.12 | 101.0448 | 13.1 | 6.79 | 27.1432 | YES | 438.2
7 | 0.55 | 187.64 | 103.202 | 13.2 | 6.79 | 26.9929 | YES | 437
8 | 0.57 | 189.43 | 107.9751 | 13.4 | 6.75 | 26.3003 | YES | 442.2
9 | 0.58 | 187.12 | 108.5296 | 13.4 | 6.79 | 26.7252 | YES | 438.2
10 | 0.57 | 186.36 | 106.2252 | 13.3 | 6.77 | 26.6749 | YES | 440
11 | 0.58 | 187.85 | 108.953 | 13.4 | 6.74 | 26.2326 | YES | 436.5
12 | 0.58 | 187.42 | 108.7036 | 13.5 | 6.82 | 26.8448 | YES | 437.5
13 | 0.58 | 187.42 | 108.7036 | 13.4 | 6.8 | 26.8248 | YES | 437.5
14 | 0.54 | 188.15 | 101.601 | 13.6 | 6.84 | 26.742 | YES | 435.8
15 | 0.62 | 187.55 | 116.281 | 13.1 | 6.86 | 28.1145 | YES | 437.2
16 | 0.63 | 186.45 | 117.4635 | 13.2 | 6.79 | 27.2409 | YES | 439.8
17 | 0.63 | 187.3 | 117.999 | 13.4 | 6.83 | 27.2813 | YES | 437.8
18 | 0.63 | 187.38 | 118.0494 | 13.3 | 6.81 | 27.2611 | YES | 436.2
19 | 0.63 | 186.81 | 117.6903 | 13.4 | 6.8 | 26.9787 | YES | 438.8
20 | 0.61 | 186.57 | 113.8077 | 12.9 | 6.81 | 27.9368 | YES | 439.5
21 | 0.57 | 187.21 | 106.7097 | 12.9 | 6.81 | 27.8094 | YES | 438
22 | 0.63 | 189.85 | 119.6055 | 12.9 | 6.84 | 28.3145 | YES | 441.2
23 | 0.65 | 187.3 | 121.745 | 13.1 | 6.81 | 27.6917 | YES | 437.8
24 | 0.6 | 187.3 | 112.38 | 13.1 | 6.83 | 27.7394 | YES | 437.8
25 | 0.61 | 187 | 114.07 | 12.8 | 6.8 | 28.02 | YES | 438.5
26 | 0.61 | 186.57 | 113.8077 | 13 | 6.8 | 27.6476 | YES | 439.5
27 | 0.6 | 186.57 | 111.942 | 12.8 | 6.87 | 28.7252 | YES | 439.5
28 | 0.43 | 187.64 | 80.6852 | 12.6 | 6.84 | 28.2359 | YES | 437
29 | 0.6 | 188.59 | 113.154 | 12.7 | 6.85 | 28.7039 | YES | 434.8
30 | 0.61 | 188.15 | 114.7715 | 12.8 | 6.83 | 28.334 | YES | 435.8
31 | 0.6 | 186.78 | 112.068 | 12.6 | 6.8 | 28.3649 | YES | 439
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2