## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lane
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-03-01
System Name: | Rainbow Water District |  |  | ID#: 4100839 |  | WTP ID: TP- | Chase
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 113 |  | 12.6 | 25 | 0.019 | 0.02
2 | 114 |  | 12.6 | 25 | 0.019 | 0.02
3 | 114 |  | 12.5 | 25 | 0.019 | 0.02
4 | 115 |  | 12.3 | 25 | 0.02 | 0.02
5 | 114 |  | 12.6 | 25 | 0.019 | 0.02
6 | 114 |  | 12.5 | 25 | 0.02 | 0.02
7 | 114 |  | 12.7 | 25 | 0.017 | 0.02
8 | 114 |  | 12.5 | 25 | 0.02 | 0.02
9 | 114 |  | 12.2 | 25 | 0.02 | 0.02
10 | 114 |  | 12 | 25 | 0.017 | 0.02
11 | 116 |  | 12.2 | 25 | 0.02 | 0.02
12 | 115 |  | 12 | 25 | 0.02 | 0.02
13 | 114 |  | 11.7 | 25 | 0.02 | 0.02
14 | 114 |  | 12.1 | 25 | 0.02 | 0.02
15 | 115 |  | 12.3 | 25 | 0.02 | 0.02
16 | 115 |  | 12.8 | 25 | 0.02 | 0.047
17 | 93 |  | offline | 25 | offline | offline
18 | 114 |  | 11.9 | 25 | 0.026 | 0.04
19 | 115 |  | 12.1 | 25 | 0.02 | 0.02
20 | 114 |  | 11.9 | 25 | 0.02 | 0.02
21 | 114 |  | 12.3 | 25 | 0.017 | 0.02
22 | 114 |  | 12.8 | 25 | 0.021 | 0.047
23 | 115 |  | 13 | 25 | 0.026 | 0.04
24 | 115 |  | 13.3 | 25 | 0.072 | 0.029
25 | 118 |  | 14.2 | 25 | 0.03 | 0.033
26 | 119 |  | 14.5 | 25 | 0.026 | 0.033
27 | 119 |  | 16 | 25 | 0.026 | 0.027
28 | 118 |  | 14.8 | 25 | 0.028 | 0.52
29 | 117 |  | 15.6 | 25 | 0.027 | 0.027
30 | 119 |  | 16.1 | 25 | 0.02 | 0.027
31 | 120 |  | 16.8 | 25 | 0.02 | 0.02
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:Eric Carlson
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE:4/4/25
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 541 ) 746-1676 |  | CERT #: T-09011
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Chase
System Name: | Rainbow Water District |  | ID#: 4100839 |  | Month/Year: | 2025-03-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.72 | 188.41 | 135.6552 | 12.3 | 6.31 | 25.6812 | YES | 435.2
2 | 0.72 | 188.59 | 135.7848 | 12.37 | 6.34 | 25.8223 | YES | 434.8
3 | 0.73 | 188.59 | 137.6707 | 12.4 | 6.32 | 25.6349 | YES | 434.8
4 | 0.71 | 181 | 128.51 | 12.26 | 6.31 | 25.7171 | YES | 438.5
5 | 0.54 | 187.72 | 101.3688 | 12.3 | 6.38 | 25.7829 | YES | 436.8
6 | 0.66 | 188.27 | 124.2582 | 12.31 | 6.3 | 25.4229 | YES | 440.2
7 | 0.68 | 187.3 | 127.364 | 12.4 | 6.32 | 25.5016 | YES | 437.8
8 | 0.69 | 189.46 | 130.7274 | 12.36 | 6.32 | 25.5905 | YES | 432.8
9 | 0.69 | 188.07 | 129.7683 | 12.34 | 6.31 | 25.5387 | YES | 436
10 | 0.69 | 187.98 | 129.7062 | 12.34 | 6.29 | 25.3736 | YES | 436.2
11 | 0.67 | 188.72 | 126.4424 | 12.25 | 6.35 | 25.9609 | YES | 434.5
12 | 0.68 | 187.55 | 127.534 | 12.21 | 6.35 | 26.0517 | YES | 437.2
13 | 0.69 | 187.3 | 129.237 | 12.18 | 6.32 | 25.8729 | YES | 437.8
14 | 0.68 | 187.98 | 127.8264 | 12.28 | 6.36 | 26.0251 | YES | 436.2
15 | 0.69 | 188.72 | 130.2168 | 12.05 | 6.29 | 25.8258 | YES | 434.2
16 | 0.69 | 188.5 | 130.065 | 11.56 | 6.34 | 27.0514 | YES | 438
17 | offline | offline | #VALUE! | 11.58 | 6.38 | #VALUE! | #VALUE! | offline
18 | 0.55 | 187.72 | 103.246 | 12.9 | 6.3 | 22.943 | YES | 436.8
19 | 0.67 | 189.02 | 126.6434 | 12.4 | 6.3 | 25.3105 | YES | 433.8
20 | 0.66 | 187 | 123.42 | 12.59 | 6.31 | 23.8132 | YES | 438.5
21 | 0.65 | 181.3 | 117.845 | 12.55 | 6.32 | 23.9392 | YES | 437.8
22 | 0.66 | 187.64 | 123.8424 | 12.57 | 6.3 | 23.7564 | YES | 437
23 | 0.63 | 187.98 | 118.4274 | 12.2 | 6.33 | 25.7635 | YES | 436.2
24 | 0.61 | 188.59 | 115.0399 | 12.4 | 6.33 | 25.3985 | YES | 434.8
25 | 0.59 | 189.28 | 111.6752 | 12.1 | 6.34 | 25.8972 | YES | 433.2
26 | 0.58 | 188.28 | 109.2024 | 12.12 | 6.35 | 25.9227 | YES | 435.5
27 | 0.54 | 187.64 | 101.3256 | 12.11 | 6.29 | 25.3322 | YES | 437
28 | 0.51 | 188.07 | 95.9157 | 12.25 | 6.36 | 25.6138 | YES | 436
29 | 0.58 | 187.21 | 108.5818 | 12.03 | 6.31 | 25.7287 | YES | 438
30 | 0.57 | 188.15 | 107.2455 | 12.05 | 6.33 | 25.8379 | YES | 435.8
31 | 0.57 | 168.72 | 96.1704 | 12.2 | 6.32 | 25.5197 | YES | 486
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2