## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lane
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-04-01
System Name: | Rainbow Water District |  |  | ID#: 4100839 |  | WTP ID: TP- | Chase
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 118 |  | 15.8 | 25 | 0.02 | 0.028
2 | 120 |  | 16.9 | 25 | 0.02 | 0.02
3 | 120 |  | 17.9 | 25 | 0.02 | 0.022
4 | 121 |  | 18.1 | 25 | 0.019 | 0.02
5 | 120 |  | 17.9 | 25 | 0.02 | 0.02
6 | 121 |  | 17.9 | 25 | 0.019 | 0.02
7 | 122 |  | 18.2 | 25 | 0.02 | 0.02
8 | 122 |  | 18.6 | 25 | 0.019 | 0.02
9 | Offline |  | offline | 25 | offline | offline
10 | 104 |  | 0.3 | 25 | 0.044 | 0.047
11 | 104 |  | 0.4 | 25 | 0.047 | 0.058
12 | 104 |  | 0.4 | 25 | 0.056 | 0.056
13 | 102 |  | 0.41 | 25 | 0.048 | 0.106
14 | 106 |  | 0.42 | 25 | 0.041 | 0.059
15 | 105 |  | 0.44 | 25 | 0.044 | 0.049
16 | 105 |  | 0.46 | 25 | 0.026 | 0.059
17 | 104 |  | 0.52 | 25 | 0.026 | 0.049
18 | 105 |  | 0.53 | 25 | 0.031 | 0.053
19 | 105 |  | 0.56 | 25 | 0.05 | 0.055
20 | 103 |  | 0.61 | 25 | 0.047 | 0.048
21 | 106 |  | 0.63 | 25 | 0.039 | 0.05
22 | 107 |  | 0.65 | 25 | 0.02 | 0.026
23 | 106 |  | 0.71 | 25 | 0.02 | 0.026
24 | 106 |  | 0.72 | 25 | 0.026 | 0.026
25 | 106 |  | 0.75 | 25 | 0.02 | 0.02
26 | 107 |  | 0.87 | 25 | 0.019 | 0.019
27 | 106 |  | 0.94 | 25 | 0.022 | 0.022
28 | 108 |  | 0.98 | 25 | 0.02 | 0.02
29 | 109 |  | 1.1 | 25 | 0.02 | 0.02
30 | 110 |  | 1.1 | 25 | 0.02 | 0.02
31
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:Eric Carlson
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE:5/5/25
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 541 ) 746-1676 |  | CERT #:T-09011
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Chase
System Name: | Rainbow Water District |  | ID#: 4100839 |  | Month/Year: | 2025-04-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.54 | 170.3 | 91.962 | 12.6 | 6.36 | 23.9139 | YES | 481.5
2 | 0.6 | 188.28 | 112.968 | 12 | 6.37 | 26.3396 | YES | 435.5
3 | 0.6 | 188.5 | 113.1 | 12.01 | 6.35 | 26.1523 | YES | 435
4 | 0.6 | 188.72 | 113.232 | 12.2 | 6.4 | 26.2749 | YES | 434.5
5 | 0.58 | 188.5 | 109.33 | 12.1 | 6.36 | 26.0391 | YES | 435
6 | 0.58 | 188.28 | 109.2024 | 12.1 | 6.35 | 25.9544 | YES | 434.5
7 | 0.58 | 187.3 | 108.634 | 11.91 | 6.36 | 26.3435 | YES | 437.8
8 | 0.58 | 188.12 | 109.1096 | 12 | 6.39 | 26.4566 | YES | 434.5
9 | offline | offline | #VALUE! | offline | offline | #VALUE! | #VALUE! | offline
10 | 0.45 | 186.66 | 83.997 | 12.6 | 6.39 | 23.9347 | YES | 434.3
11 | 0.6 | 184.26 | 110.556 | 11.96 | 6.33 | 26.062 | YES | 445
12 | 0.62 | 186.15 | 115.413 | 12.3 | 6.35 | 25.7469 | YES | 440.5
13 | 0.6 | 185.31 | 111.186 | 12.4 | 6.38 | 25.7872 | YES | 442.5
14 | 0.49 | 187.64 | 91.9436 | 12.2 | 6.36 | 25.6384 | YES | 437
15 | 0.61 | 184.76 | 112.7036 | 12.4 | 6.37 | 25.7304 | YES | 443.8
16 | 0.6 | 185.52 | 111.312 | 12.2 | 6.36 | 25.9347 | YES | 442
17 | 0.62 | 187.72 | 116.3864 | 12.2 | 6.35 | 25.9045 | YES | 436.8
18 | 0.62 | 185.94 | 115.2828 | 12.3 | 6.37 | 25.9149 | YES | 441
19 | 0.62 | 186.78 | 115.8036 | 12.15 | 6.26 | 25.2356 | YES | 439
20 | 0.64 | 186.02 | 119.0528 | 12.2 | 6.35 | 25.9588 | YES | 440.8
21 | 0.64 | 186.36 | 119.2704 | 12.1 | 6.42 | 26.7219 | YES | 440
22 | 0.64 | 186.87 | 119.5968 | 12.2 | 6.4 | 26.3854 | YES | 438.8
23 | 0.64 | 186.44 | 119.3216 | 12.3 | 6.32 | 25.5506 | YES | 439.8
24 | 0.64 | 186.15 | 119.136 | 12.2 | 6.33 | 25.7904 | YES | 440.5
25 | 0.64 | 184.35 | 117.984 | 12.23 | 6.3 | 25.4938 | YES | 444.8
26 | 0.65 | 188.15 | 122.2975 | 12.4 | 6.38 | 25.9223 | YES | 435.8
27 | 0.65 | 185.52 | 120.588 | 12.2 | 6.38 | 26.2412 | YES | 442
28 | 0.64 | 188.28 | 120.4992 | 12.11 | 6.34 | 26.017 | YES | 435.5
29 | 0.65 | 187.21 | 121.6865 | 11.99 | 6.32 | 26.0657 | YES | 438
30 | 0.64 | 187.42 | 119.9488 | 11.99 | 6.37 | 26.4666 | YES | 437.5
31
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2