## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lane
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-05-01
System Name: | Rainbow Water District |  |  | ID#: 4100839 |  | WTP ID: TP- | Chase
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 111 |  | 1.3 | 25 | 0.019 | 0.02
2 | 110 |  | 1.3 | 25 | 0.025 | 0.02
3 | 111 |  | 1.31 | 25 | 0.02 | 0.02
4 | 112 |  | 1.32 | 25 | 0.02 | 0.02
5 | 112 |  | 1.3 | 25 | 0.02 | 0.02
6 | 113 |  | 1.3 | 25 | 0.019 | 0.02
7 | 90 |  | 1.7 | 25 | 0.019 | 0.02
8 | 112 |  | 1.5 | 25 | 0.019 | 0.076
9 | 113 |  | 1.49 | 25 | 0.019 | 0.02
10 | 113 |  | 1.5 | 25 | 0.019 | 0.02
11 | 115 |  | 1.5 | 25 | 0.02 | 0.02
12 | 117 |  | 1.5 | 25 | 0.019 | 0.02
13 | 117 |  | 1.55 | 25 | 0.02 | 0.02
14 | 118 |  | 1.55 | 25 | 0.019 | 0.02
15 | 119 |  | 1.56 | 25 | 0.02 | 0.02
16 | 119 |  | 1.6 | 25 | 0.02 | 0.02
17 | 118 |  | 1.61 | 25 | 0.018 | 0.02
18 | 119 |  | 1.61 | 25 | 0.019 | 0.019
19 | 119 |  | 1.61 | 25 | 0.019 | 0.02
20 | 120 |  | 1.7 | 25 | 0.02 | 0.02
21 | 121 |  | 1.7 | 25 | 0.02 | 0.02
22 | 121 |  | 1.7 | 25 | 0.019 | 0.02
23 | 123 |  | 1.65 | 25 | 0.019 | 0.02
24 | 122 |  | 1.71 | 25 | 0.019 | 0.02
25 | 123 |  | 1.72 | 25 | 0.019 | 0.02
26 | 124 |  | 1.76 | 25 | 0.019 | 0.02
27 | 125 |  | 1.74 | 25 | 0.019 | 0.02
28 | 126 |  | 1.8 | 25 | 0.019 | 0.02
29 | 127 |  | 1.8 | 25 | 0.019 | 0.02
30 | 127 |  | 1.79 | 25 | 0.019 | 0.02
31 | 126 |  | 1.5 | 25 | 0.019 | 0.019
Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:Eric Carlson
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE:6/9/25
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 541 ) 954-9941 |  | CERT #:T-09011
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Chase
System Name: | Rainbow Water District |  | ID#: 4100839 |  | Month/Year: | 2025-05-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.63 | 186.57 | 117.5391 | 11.98 | 6.38 | 26.5416 | YES | 439.5
2 | 0.65 | 187.55 | 121.9075 | 12.02 | 6.33 | 26.1028 | YES | 437.2
3 | 0.65 | 188.5 | 122.525 | 12.1 | 6.34 | 26.0602 | YES | 435
4 | 0.66 | 187.64 | 123.8424 | 12.2 | 6.4 | 26.4408 | YES | 437
5 | 0.66 | 188.07 | 124.1262 | 12.07 | 6.34 | 26.1354 | YES | 436
6 | 0.64 | 188.15 | 120.416 | 12.15 | 6.39 | 26.38 | YES | 435.8
7 | 0.63 | 169.49 | 106.7787 | 12.3 | 6.28 | 25.1953 | YES | 483.8
8 | 0.63 | 187.3 | 117.999 | 12.19 | 6.34 | 25.8632 | YES | 437.8
9 | 0.66 | 187.85 | 123.981 | 12.21 | 6.41 | 26.5111 | YES | 436.5
10 | 0.66 | 188.59 | 124.4694 | 12.26 | 6.33 | 25.7499 | YES | 434.8
11 | 0.65 | 187.64 | 121.966 | 12.26 | 6.3 | 25.4738 | YES | 437
12 | 0.67 | 187.56 | 125.6652 | 12.24 | 6.31 | 25.6412 | YES | 437.2
13 | 0.68 | 187.56 | 127.5408 | 12.32 | 6.36 | 25.9616 | YES | 437.2
14 | 0.68 | 188.07 | 127.8876 | 12.41 | 6.38 | 25.9879 | YES | 436
15 | 0.67 | 188.28 | 126.1476 | 12.44 | 6.36 | 25.7452 | YES | 435.5
16 | 0.66 | 187.85 | 123.981 | 12.44 | 6.37 | 25.8021 | YES | 436.5
17 | 0.65 | 187.64 | 121.966 | 12.45 | 6.33 | 25.4271 | YES | 437
18 | 0.65 | 188.15 | 122.2975 | 12.5 | 6.4 | 24.7475 | YES | 435.8
19 | 0.68 | 188.5 | 128.18 | 12.5 | 6.36 | 24.465 | YES | 435
20 | 0.5 | 187.3 | 93.65 | 12.72 | 6.5 | 24.8795 | YES | 437.8
21 | 0.62 | 188.28 | 116.7336 | 12.68 | 6.45 | 24.8248 | YES | 435.5
22 | 0.61 | 187.3 | 114.253 | 12.64 | 6.34 | 23.8633 | YES | 437.8
23 | 0.62 | 187.64 | 116.3368 | 12.7 | 6.49 | 25.1639 | YES | 437
24 | 0.62 | 187.64 | 116.3368 | 12.8 | 6.48 | 24.9026 | YES | 437
25 | 0.62 | 189.02 | 117.1924 | 12.8 | 6.48 | 24.9026 | YES | 433.8
26 | 0.62 | 188.41 | 116.8142 | 12.9 | 6.48 | 24.736 | YES | 435.2
27 | 0.62 | 187.64 | 116.3368 | 12.9 | 6.52 | 25.1076 | YES | 437
28 | 0.61 | 188.28 | 114.8508 | 12.88 | 6.49 | 24.8332 | YES | 435.5
29 | 0.63 | 188.41 | 118.6983 | 13 | 6.5 | 24.7828 | YES | 435.7
30 | 0.62 | 189.15 | 117.273 | 13.1 | 6.54 | 24.9582 | YES | 433.5
31 | 0.64 | 213.54 | 136.6656 | 13.01 | 6.52 | 24.9801 | YES | 384
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2