## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lane
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-06-01
System Name: | Rainbow Water District |  |  | ID#: 4100839 |  | WTP ID: TP- | Chase
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 126 |  | 1.5 | 25 | 0.02 | 0.02
2 | 126 |  | 1.5 | 25 | 0.02 | 0.02
3 | 128 |  | 1.4 | 25 | 0.02 | 0.02
4 | 128 |  | 1.5 | 25 | 0.019 | 0.025
5 | 103 |  | 1.2 | 25 | 0.019 | 0.11
6 | 102 |  | 1.5 | 25 | 0.019 | 0.019
7 | 101 |  | 1.8 | 25 | 0.018 | 0.018
8 | 103 |  | 1.8 | 25 | 0.019 | 0.019
9 | 101 |  | 1.7 | 25 | 0.019 | 0.019
10 | 103 |  | 1.8 | 25 | 0.019 | 0.019
11 | 102 |  | 1.8 | 25 | 0.019 | 0.02
12 | 103 |  | 1.9 | 25 | 0.019 | 0.021
13 | 105 |  | 1.9 | 25 | 0.019 | 0.02
14 | 103 |  | 1.9 | 25 | 0.019 | 0.02
15 | 104 |  | 1.9 | 25 | 0.019 | 0.02
16 | 104 |  | 2 | 25 | 0.019 | 0.02
17 | 104 |  | 2 | 25 | 0.019 | 0.02
18 | 104 |  | 1.8 | 25 | 0.022 | 0.026
19 | 104 |  | 1.9 | 25 | 0.026 | 0.026
20 | 104 |  | 2 | 25 | 0.019 | 0.02
21 | 104 |  | 2.1 | 25 | 0.02 | 0.02
22 | 104 |  | 2.1 | 25 | 0.02 | 0.02
23 | 104 |  | 2 | 25 | 0.019 | 0.02
24 | 105 |  | 2 | 25 | 0.019 | 0.02
25 | 105 |  | 2 | 25 | 0.019 | 0.019
26 | 103 |  | 2 | 25 | 0.019 | 0.02
27 | 103 |  | 2.1 | 25 | 0.019 | 0.02
28 | 103 |  | 2.2 | 25 | 0.019 | 0.02
29 | 103 |  | 2.1 | 25 | 0.019 | 0.019
30 | 103 |  | 2.1 | 25 | 0.019 | 0.019
31
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:Eric Carlson
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE:7/3/25
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 541 ) 746-1676 |  | CERT #:T-09011
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Chase
System Name: | Rainbow Water District |  | ID#: 4100839 |  | Month/Year: | 2025-06-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.65 | 213.43 | 138.7295 | 13 | 6.37 | 23.6634 | YES | 384.2
2 | 0.66 | 226 | 149.16 | 13.07 | 6.5 | 24.7516 | YES | 362.8
3 | 0.66 | 226 | 149.16 | 13.1 | 6.51 | 24.794 | YES | 362.8
4 | 0.35 | 211 | 73.85 | 13.18 | 6.48 | 23.5343 | YES | 388.5
5 | 0.55 | 208 | 114.4 | 13.2 | 6.5 | 24.2287 | YES | 392.5
6 | 0.58 | 184 | 106.72 | 13.27 | 6.5 | 24.1982 | YES | 445.2
7 | 0.57 | 183 | 104.31 | 13.34 | 6.34 | 22.661 | YES | 446.2
8 | 0.57 | 187 | 106.59 | 13.64 | 6.5 | 23.5767 | YES | 437.2
9 | 0.56 | 186 | 104.16 | 13.68 | 6.45 | 23.0516 | YES | 439.5
10 | 0.56 | 185 | 103.6 | 13.81 | 6.44 | 22.7655 | YES | 441.8
11 | 0.57 | 186 | 106.02 | 13.7 | 6.21 | 21.0666 | YES | 440.8
12 | 0.59 | 185 | 109.15 | 13.81 | 6.47 | 23.1018 | YES | 441.8
13 | 0.6 | 184 | 110.4 | 13.77 | 6.35 | 22.1729 | YES | 443.8
14 | 0.62 | 186 | 115.32 | 14 | 6.52 | 23.3188 | YES | 440.8
15 | 0.62 | 186 | 115.32 | 14.1 | 6.55 | 23.4235 | YES | 439
16 | 0.61 | 183 | 111.63 | 14.1 | 6.51 | 23.0495 | YES | 445.8
17 | 0.6 | 187 | 112.2 | 14.2 | 6.55 | 23.213 | YES | 437.8
18 | 0.59 | 185 | 109.15 | 14.6 | 6.4 | 21.3377 | YES | 443
19 | 0.61 | 185 | 112.85 | 14.28 | 6.46 | 22.3499 | YES | 441.2
20 | 0.62 | 185 | 114.7 | 14.15 | 6.43 | 22.3205 | YES | 441
21 | 0.64 | 186 | 119.04 | 14.19 | 6.46 | 22.5636 | YES | 440.5
22 | 0.63 | 186 | 117.18 | 14.18 | 6.47 | 22.6373 | YES | 439.2
23 | 0.61 | 185 | 112.85 | 14.5 | 6.54 | 22.6902 | YES | 442.2
24 | 0.6 | 185 | 111 | 14.5 | 6.5 | 22.3275 | YES | 441.8
25 | 0.6 | 186 | 111.6 | 14.5 | 6.37 | 21.2664 | YES | 438.8
26 | 0.61 | 186 | 113.46 | 14.37 | 6.39 | 21.6401 | YES | 440.5
27 | 0.61 | 187 | 114.07 | 14.52 | 6.44 | 21.8273 | YES | 437
28 | 0.62 | 187 | 115.94 | 14.7 | 6.57 | 22.6653 | YES | 437
29 | 0.63 | 187 | 117.81 | 14.8 | 6.57 | 22.539 | YES | 437.8
30 | 0.63 | 185 | 116.55 | 14.7 | 6.51 | 22.1877 | YES | 441.8
31
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2