## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lane
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-07-01
System Name: | Rainbow Water District |  |  | ID#: 4100839 |  | WTP ID: TP- | Chase
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 103 |  | 2.1 | 25 | 0.019 | 0.019
2 | 103 |  | 2.3 | 25 | 0.019 | 0.019
3 | 102 |  | 2.1 | 25 | 0.019 | 0.019
4 | 102 |  | 2.1 | 25 | 0.019 | 0.019
5 | 102 |  | 2.1 | 25 | 0.019 | 0.019
6 | 102 |  | 2.2 | 25 | 0.019 | 0.019
7 | 103 |  | 2.2 | 25 | 0.019 | 0.018
8 | 103 |  | 2.1 | 25 | 0.017 | 0.018
9 | 104 |  | 2.3 | 25 | 0.019 | 0.019
10 | 102 |  | 2.3 | 25 | 0.019 | 0.019
11 | 102 |  | 2.3 | 25 | 0.019 | 0.018
12 | 101 |  | 2.2 | 25 | 0.018 | 0.018
13 | 102 |  | 2.2 | 25 | 0.017 | 0.018
14 | 102 |  | 2.2 | 25 | 0.019 | 0.019
15 | 103 |  | 2.2 | 25 | 0.019 | 0.018
16 | 103 |  | 2.4 | 25 | 0.017 | 0.026
17 | 103 |  | 2.3 | 25 | 0.017 | 0.018
18 | 103 |  | 2.3 | 25 | 0.019 | 0.019
19 | 103 |  | 2.3 | 25 | 0.017 | 0.018
20 | 103 |  | 2.3 | 25 | 0.019 | 0.02
21 | 104 |  | 2.4 | 25 | 0.019 | 0.02
22 | 103 |  | 2.4 | 25 | 0.019 | 0.02
23 | 103 |  | 2.4 | 25 | 0.019 | 0.019
24 | 104 |  | 2.4 | 25 | 0.019 | 0.019
25 | 102 |  | 2.4 | 25 | 0.02 | 0.019
26 | 104 |  | 2.4 | 25 | 0.02 | 0.019
27 | 103 |  | 2.3 | 25 | 0.02 | 0.02
28 | 103 |  | 2.5 | 25 | 0.017 | 0.02
29 | 104 |  | 2.5 | 25 | 0.02 | 0.02
30 | 104 |  | 2.5 | 25 | 0.019 | 0.018
31 | 103 |  | 2.4 | 25 | 0.017 | 0.022
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | Eric Carlson
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE: 8/6/25
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 541 ) 746-1676 |  | CERT #:T-09011
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Chase
System Name: | Rainbow Water District |  | ID#: 4100839 |  | Month/Year: | 2025-07-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.62 | 186.92 | 115.8904 | 15.1 | 6.33 | 20.1638 | YES | 438.7
2 | 0.62 | 186.02 | 115.3324 | 15.2 | 6.52 | 21.5078 | YES | 440.8
3 | 0.63 | 187.85 | 118.3455 | 14.8 | 6.3 | 20.37 | YES | 436.5
4 | 0.63 | 185.6 | 116.928 | 15.1 | 6.53 | 21.7597 | YES | 441.8
5 | 0.64 | 188.5 | 120.64 | 15.1 | 6.44 | 21.0622 | YES | 435
6 | 0.64 | 187.98 | 120.3072 | 15.2 | 6.54 | 21.7195 | YES | 436.2
7 | 0.63 | 187.12 | 117.8856 | 15.2 | 6.53 | 21.6134 | YES | 438.2
8 | 0.63 | 186.36 | 117.4068 | 15.4 | 6.54 | 21.4038 | YES | 434.8
9 | 0.63 | 186.44 | 117.4572 | 15.5 | 6.5 | 20.9433 | YES | 440
10 | 0.64 | 186.44 | 119.3216 | 15.5 | 6.44 | 20.5007 | YES | 439.8
11 | 0.64 | 184.68 | 118.1952 | 15.6 | 6.54 | 21.1411 | YES | 444
12 | 0.63 | 186.57 | 117.5391 | 15.5 | 6.46 | 20.6314 | YES | 439.5
13 | 0.63 | 186.87 | 117.7281 | 15.8 | 6.55 | 20.9118 | YES | 438.8
14 | 0.61 | 185.31 | 113.0391 | 15.9 | 6.45 | 19.9595 | YES | 442.5
15 | 0.61 | 186.02 | 113.4722 | 15.6 | 6.18 | 18.4011 | YES | 440.8
16 | 0.61 | 186.78 | 113.9358 | 15.9 | 6.46 | 20.0346 | YES | 439
17 | 0.61 | 185.6 | 113.216 | 15.9 | 6.27 | 18.6524 | YES | 441.8
18 | 0.61 | 186.87 | 113.9907 | 15.8 | 6.22 | 18.4288 | YES | 438.8
19 | 0.63 | 185.01 | 116.5563 | 16 | 6.51 | 20.3237 | YES | 443.2
20 | 0.63 | 184.26 | 116.0838 | 16 | 6.24 | 18.3604 | YES | 445
21 | 0.63 | 185.31 | 116.7453 | 16 | 6.5 | 20.2475 | YES | 442.5
22 | 0.63 | 185.85 | 117.0855 | 16.1 | 6.47 | 19.8856 | YES | 441.2
23 | 0.63 | 186.87 | 117.7281 | 16.2 | 6.54 | 20.2779 | YES | 438.8
24 | 0.62 | 185.6 | 115.072 | 16.6 | 6.56 | 19.8624 | YES | 441.8
25 | 0.62 | 187.64 | 116.3368 | 16.3 | 6.22 | 17.8341 | YES | 437
26 | 0.62 | 188.07 | 116.6034 | 16.5 | 6.52 | 19.6989 | YES | 436
27 | 0.63 | 187.64 | 118.2132 | 16.3 | 6.25 | 18.0581 | YES | 437
28 | 0.63 | 186.36 | 117.4068 | 16.5 | 6.52 | 19.7217 | YES | 440
29 | 0.63 | 186.78 | 117.6714 | 16.7 | 6.57 | 19.8257 | YES | 439
30 | 0.63 | 186.57 | 117.5391 | 16.6 | 6.53 | 19.6624 | YES | 439.5
31 | 0.63 | 185.86 | 117.0918 | 16.5 | 6.5 | 19.5739 | YES | 441.2
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2