## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lane
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-08-01
System Name: | Rainbow Water District |  |  | ID#: 4100839 |  | WTP ID: TP- | Chase
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 104 |  | 2.4 | 25 | 0.02 | 0.02
2 | 103 |  | 2.4 | 25 | 0.018 | 0.018
3 | 102 |  | 2.5 | 25 | 0.018 | 0.02
4 | 104 |  | 2.6 | 25 | 0.019 | 0.019
5 | 104 |  | 2.6 | 25 | 0.02 | 0.02
6 | 104 |  | 2.6 | 25 | 0.02 | 0.024
7 | 105 |  | 2.6 | 25 | 0.019 | 0.02
8 | 103 |  | 2.7 | 25 | 0.019 | 0.019
9 | 104 |  | 2.6 | 25 | 0.019 | 0.019
10 | 103 |  | 2.6 | 25 | 0.019 | 0.07
11 | 103 |  | 2.8 | 25 | 0.019 | 0.019
12 | 104 |  | 2.7 | 25 | 0.019 | 0.019
13 | 104 |  | 2.7 | 25 | 0.019 | 0.019
14 | 104 |  | 2.8 | 25 | 0.019 | 0.019
15 | 104 |  | 2.6 | 25 | 0.019 | 0.019
16 | 104 |  | 2.7 | 25 | 0.018 | 0.02
17 | 104 |  | 2.7 | 25 | 0.019 | 0.02
18 | 105 |  | 2.8 | 25 | 0.019 | 0.02
19 | 105 |  | 2.9 | 25 | 0.019 | 0.021
20 | 105 |  | 2.9 | 25 | 0.019 | 0.019
21 | 105 |  | 2.6 | 25 | 0.017 | 0.02
22 | 104 |  | 2.7 | 25 | 0.019 | 0.02
23 | 103 |  | 2.8 | 25 | 0.019 | 0.019
24 | 104 |  | 2.9 | 25 | 0.019 | 0.019
25 | 104 |  | 2.8 | 25 | 0.019 | 0.019
26 | 103 |  | 2.9 | 25 | 0.019 | 0.019
27 | 103 |  | 2.9 | 25 | 0.019 | 0.024
28 | 105 |  | 2.9 | 25 | 0.019 | 0.019
29 | 104 |  | 2.9 | 25 | 0.019 | 0.021
30 | 102 |  | 2.9 | 25 | 0.019 | 0.02
31 | 103 |  | 2.9 | 25 | 0.018 | 0.019
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:Eric Carlson
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE:9/4/25
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 541 ) 746-1676 |  | CERT #:T-09011
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Chase
System Name: | Rainbow Water District |  | ID#: 4100839 |  | Month/Year: | 2025-08-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.63 | 186.02 | 117.1926 | 16.7 | 6.55 | 19.6772 | YES | 440.8
2 | 0.63 | 186.27 | 117.3501 | 16.3 | 6.22 | 17.8548 | YES | 440.2
3 | 0.49 | 185.31 | 90.8019 | 16.4 | 6.3 | 17.9829 | YES | 442.5
4 | 0.57 | 187.21 | 106.7097 | 16.7 | 6.57 | 19.6887 | YES | 438
5 | 0.57 | 185.94 | 105.9858 | 16.55 | 6.47 | 19.1554 | YES | 441
6 | 0.58 | 186.45 | 108.141 | 16.6 | 6.23 | 17.4588 | YES | 439.8
7 | 0.63 | 185.73 | 117.0099 | 16.8 | 6.57 | 19.6919 | YES | 441.5
8 | 0.61 | 186.7 | 113.887 | 16.7 | 6.53 | 19.4846 | YES | 439.2
9 | 0.6 | 187.12 | 112.272 | 16.74 | 6.55 | 19.556 | YES | 438.2
10 | 0.58 | 187.98 | 109.0284 | 16.59 | 6.18 | 17.1435 | YES | 436.2
11 | 0.58 | 187 | 108.46 | 16.9 | 6.5 | 18.9407 | YES | 438.5
12 | 0.58 | 187.43 | 108.7094 | 17 | 6.56 | 19.2425 | YES | 437.5
13 | 0.58 | 186.79 | 108.3382 | 16.9 | 6.46 | 18.6574 | YES | 439
14 | 0.6 | 186.36 | 111.816 | 16.9 | 6.47 | 18.7713 | YES | 440
15 | 0.6 | 187.21 | 112.326 | 16.7 | 6.24 | 17.4465 | YES | 438
16 | 0.6 | 185.6 | 111.36 | 16.7 | 6.34 | 18.1178 | YES | 441.8
17 | 0.61 | 188.16 | 114.7776 | 16.7 | 6.51 | 19.3386 | YES | 435.8
18 | 0.61 | 185.52 | 113.1672 | 16.9 | 6.54 | 19.2949 | YES | 442
19 | 0.62 | 186.03 | 115.3386 | 16.8 | 6.5 | 19.158 | YES | 440.8
20 | 0.62 | 187.64 | 116.3368 | 16.9 | 6.5 | 19.0286 | YES | 437
21 | 0.61 | 186.87 | 113.9907 | 16.83 | 6.48 | 18.9537 | YES | 438.8
22 | 0.6 | 187.21 | 112.326 | 16.78 | 6.49 | 19.0677 | YES | 438
23 | 0.58 | 186.7 | 108.286 | 16.71 | 6.16 | 16.8758 | YES | 439.2
24 | 0.59 | 187.85 | 110.8315 | 16.72 | 6.17 | 16.9479 | YES | 436.5
25 | 0.58 | 186.87 | 108.3846 | 16.82 | 6.62 | 19.9229 | YES | 438.8
26 | 0.59 | 187.3 | 110.507 | 16.77 | 6.61 | 19.9385 | YES | 437.8
27 | 0.59 | 186.02 | 109.7518 | 16.57 | 6.59 | 20.0588 | YES | 440.8
28 | 0.6 | 184.76 | 110.856 | 16.97 | 6.9 | 21.9567 | YES | 443.8
29 | 0.6 | 186.27 | 111.762 | 16.67 | 6.57 | 19.7972 | YES | 440.2
30 | 0.61 | 186.57 | 113.8077 | 16.72 | 6.84 | 21.859 | YES | 439.5
31 | 0.61 | 186.02 | 113.4722 | 16.74 | 6.65 | 20.3283 | YES | 440.8
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2