## Sheet1
OHA - Drinking Water Program - Turbidity Monitoring Report Form County: Marion Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems
System Name: Stayton Water Supply ID #: OR4100843 WTP-: WTP-A Month/Year: JULY 2025
| DAY | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | Noon [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day ¹ [NTU]
| 1 |  |  | 0.18 |  |  |  | 0.23
| 2 |  |  | 0.17 |  |  |  | 0.25
| 3 |  |  | 0.16 |  |  |  | 0.2
| 4 |  |  |  | 0.16 |  |  | 0.19
| 5 |  |  |  | 0.16 |  |  | 0.17
| 6 |  |  |  | 0.15 |  |  | 0.17
| 7 |  |  | 0.17 |  |  |  | 0.22
| 8 |  |  | 0.16 |  |  |  | 0.17
| 9 |  |  | 0.16 |  |  |  | 0.24
| 10 |  |  | 0.15 |  |  |  | 0.23
| 11 |  |  | 0.16 |  |  |  | 0.27
| 12 |  |  |  | 0.19 |  |  | 0.19
| 13 |  |  |  | 0.17 |  |  | 0.2
| 14 |  |  | 0.16 |  |  |  | 0.27
| 15 |  |  | 0.19 |  |  |  | 0.2
| 16 |  |  | 0.16 |  |  |  | 0.18
| 17 |  |  | 0.19 |  |  |  | 0.2
| 18 |  |  | 0.18 |  |  |  | 0.19
| 19 |  |  |  | 0.17 |  |  | 0.18
| 20 |  |  |  | 0.16 |  |  | 0.17
| 21 |  |  | 0.15 |  |  |  | 0.18
| 22 |  |  |  | 0.15 |  |  | 0.18
| 23 |  |  | 0.16 |  |  |  | 0.18
| 24 |  |  | 0.16 |  |  |  | 0.18
| 25 |  |  | 0.17 |  |  |  | 0.18
| 26 |  |  |  | 0.15 |  |  | 0.17
| 27 |  |  |  | 0.14 |  |  | 0.16
| 28 |  |  | 0.14 |  |  |  | 0.23
| 29 |  |  | 0.13 |  |  |  | 0.26
| 30 |  |  | 0.14 |  |  |  | 0.28
| 31 |  |  | 0.16 |  |  |  | 0.31
Slow Sand Filter |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? ² YES All daily turbidity readings ≤ 5 NTU? YES |  |  |  |  | CT's met everyday? YES |  | All CL2 residuals at entry point ≤ 0.2 mg/l? YES
Notes: Turbidity from the filters |  |  |  |  | Printed Name: Michael D. Bradley
[5 empty] | Signature: Michael D. Bradley |  |  | Date: 08-01-2025
[5 empty] | Phone #: (503) 769 6907 |  |  | Cert #: 6619
¹ Including continuous turbidity data, if applicable, for optimization recording purposes. Compliance values in columns "12 AM" through "8 PM" may not correspond to continuous readings' maximum. ² Filtered systems only. Page 1 of 2

## Sheet1 (2)
OHA - Drinking Water Program - Surface Water Quality Data Form
Stayton Water Supply ID #: OR4100843 WTP-: WTP-A Month/Year: JULY 2025
Date / Time | Minimum Cl2 Residual at 1st User ( C )³ | Contact Time ( T ) | Actual CT | Temp | pH | Required CT | CT Met? ³ | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [C˚] |  | Use tables | Yes / No | [GPM]
1/ 08:00 A.M. | 1.27 | 75 | 102 | 20.2 | 732 | 21 | YES | 2100
2/ 08:00 A.M. | 1.37 | 75 | 103 | 20.7 | 7.26 | 19 | YES | 2100
3/ 08:00 A.M. | 1.11 | 75 | 83 | 21.1 | 7.19 | 19 | YES | 2100
4/ 1120 HRS | 1.34 | 75 | 101 | 20.7 | 7.25 | 19 | YES | 2100
5/ 1120 HRS | 1.3 | 75 | 98 | 20 | 7.33 | 21 | YES | 2100
6/ 1140 HRS | 1.34 | 75 | 101 | 19.8 | 7.34 | 21 | YES | 2100
7/ 8:00 A.M. | 1.33 | 75 | 100 | 20.6 | 7.35 | 20 | YES | 2100
8/ 8:00 A.M. | 1.31 | 75 | 98 | 20.4 | 7.3 | 21 | YES | 2100
9/08:00 A.M. | 1.36 | 75 | 102 | 21.2 | 7.32 | 19 | YES | 2100
10/ 08:00 A.M. | 1.01 | 75 | 76 | 20.7 | 7.3 | 19 | YES | 2100
11/ 08:00 A.M. | 1.25 | 75 | 94 | 21.4 | 7.31 | 19 | YES | 2100
12/ 1050 HRS | 1.32 | 75 | 99 | 21.1 | 7.34 | 19 | YES | 2100
13/ 1130 HRS | 1.42 | 75 | 107 | 21.9 | 7.32 | 18 | YES | 2100
14/ 08:00 AM | 1.47 | 75 | 110 | 21.1 | 7.24 | 17 | YES | 2100
15/ 8:00 A.M. | 1.48 | 75 | 111 | 22.2 | 7.3 | 18 | YES | 2100
16/ 8:00 A.M. | 1.2 | 75 | 90 | 22.2 | 7.29 | 18 | YES | 2100
17/ 8:00 A.M. | 1.29 | 75 | 97 | 21.8 | 7.36 | 19 | YES | 2100
18/ 8:00 A.M. | 1.25 | 75 | 94 | 21.8 | 7.35 | 19 | YES | 2100
19/ 1030 HRS | 1.28 | 75 | 96 | 21.1 | 7.33 | 19 | YES | 2100
20/ 1115 HRS | 1.2 | 75 | 90 | 21.8 | 7.36 | 19 | YES | 2100
21/ 8:00 A.M. | 1.39 | 75 | 104 | 20.8 | 7.34 | 19 | YES | 2100
22/ 1120 HRS | 1.18 | 75 | 89 | 19.3 | 7.34 | 21 | YES | 2100
23/ 0850 HRS | 1.22 | 75 | 92 | 19.9 | 7.34 | 21 | YES | 2100
24/ 0905 HRS | 1.15 | 75 | 86 | 20.9 | 7.3 | 19 | YES | 2100
25/ 0930 HRS | 1.42 | 75 | 107 | 20.9 | 7.32 | 19 | YES | 2100
26/ 1200 HRS | 1.24 | 75 | 93 | 21 | 7.31 | 19 | YES | 2100
27/ 1130 HRS | 1.22 | 75 | 92 | 21.2 | 7.37 | 20 | YES | 2100
28/0800 HRS | 0.96 | 75 | 72 | 20.1 | 7.31 | 21 | YES | 2100
29/ 0800 HRS | 1.16 | 75 | 87 | 20.5 | 7.37 | 20 | YES | 2100
30/ 08:00 AM | 1.29 | 75 | 97 | 20.1 | 7.35 | 21 | YES | 2100
31/ 08:00 AM | 1.28 | 75 | 96 | 20.3 | 7.34 | 21 | YES | 2100
³ If Cl₂ at entry point < 0.2 mg/L or CT not met, notify DWP by end of next business day. Page 2 of 2