## Sheet1
OHA - Drinking Water Program - Turbidity Monitoring Report Form County: Linn Conventional Filtration
Sweet Home, City of |  |  |  | I.D. # OR4100851 |  |  | WTP: WTP-B |  | Month of | 2024-02-01 |  |  |  | Required Log inactivation: |  | 0.5
| TURBIDITY | [5 empty] | Highest | Peak Hourly | Min.Cl2 Res. | CONTACT | ACTUAL | TEMP |  | REQ. | CT | log *
| 12AM | 4AM | 8AM | NOON | 4PM | 8PM | Reading of Day 1 | Demand Flow | at 1st user | TIME | (CT) |  | pH | CT | MET? | inacti-
DATE | NTU | NTU | NTU | NTU | NTU | NTU | (NTU) | (gpm) | Mg/L (C)3 | MIN. (T) | C X T | Co |  | Formula | Y / N | vation
1 | NF | 0.02 | 0.02 | NF | 0.02 | 0.02 | 0.07 | 1872 | 0.73 | 150.2393 | 109.6747 | 11.5 | 7.49 | 20.129 | Y |  | 5
2 | NF | NF | NF | 0.02 | NF | NF | 0.02 | 1858 | 0.71 | 151.3714 | 107.4737 | 12.4 | 7.62 | 19.8143 | Y |  | 5
3 | NF | NF | 0.02 | 0.02 | 0.02 | 0.02 | 0.03 | 1884 | 0.71 | 149.2824 | 105.9905 | 11.5 | 7.83 | 22.6244 | Y |  | 5
4 | NF | NF | NF | 0.02 | NF | NF | 0.03 | 1887 | 0.67 | 149.045 | 99.8602 | 11 | 7.81 | 23.1166 | Y |  | 5
5 | NF | NF | 0.02 | 0.02 | 0.03 | NF | 0.03 | 1869 | 0.68 | 150.4805 | 102.3267 | 10.6 | 7.59 | 21.9903 | Y |  | 5
6 | NF | NF | 0.02 | 0.02 | 0.02 | 0.02 | 0.04 | 1871 | 0.68 | 150.3196 | 102.2173 | 10.8 | 7.81 | 23.4521 | Y |  | 5
7 | NF | NF | NF | 0.02 | 0.02 | NF | 0.03 | 1879 | 0.68 | 149.6796 | 101.7821 | 10.6 | 7.59 | 21.9903 | Y |  | 5
8 | NF | NF | 0.03 | 0.02 | 0.02 | 0.02 | 0.03 | 1887 | 0.68 | 149.045 | 101.3506 | 12 | 7.35 | 18.4607 | Y |  | 5
9 | NF | NF | NF | 0.02 | 0.02 | 0.02 | 0.03 | 1882 | 0.71 | 149.441 | 106.1031 | 10.1 | 7.61 | 22.9681 | Y |  | 5
10 | NF | NF | NF | 0.02 | 0.02 | NF | 0.03 | 1877 | 0.69 | 149.8391 | 103.389 | 9.9 | 7.778 | 24.647 | Y |  | 5
11 | NF | NF | NF | 0.03 | 0.02 | 0.02 | 0.03 | 1869 | 0.67 | 150.4805 | 100.8219 | 9.8 | 7.64 | 23.5723 | Y |  | 5
12 | NF | NF | NF | 0.02 | 0.02 | NF | 0.03 | 1855 | 0.69 | 151.6162 | 104.6152 | 10.2 | 7.85 | 24.785 | Y |  | 5
13 | NF | NF | NF | 0.02 | 0.03 | 0.02 | 0.03 | 1881 | 0.68 | 149.5205 | 101.6739 | 9.5 | 7.78 | 25.3036 | Y |  | 5
14 | 0.02 | NF | NF | 0.02 | 0.02 | NF | 0.03 | 1851 | 0.67 | 151.9438 | 101.8024 | 10.5 | 7.82 | 23.9821 | Y |  | 5
15 | NF | NF | NF | 0.02 | 0.02 | 0.03 | 0.03 | 1878 | 0.63 | 149.7593 | 94.3484 | 10.1 | 7.65 | 23.0843 | Y |  | 5
16 | NF | NF | NF | 0.02 | 0.03 | 0.02 | 0.05 | 1868 | 0.67 | 150.561 | 100.8759 | 10 | 7.65 | 23.3438 | Y |  | 5
17 | NF | NF | NF | 0.03 | 0.02 | 0.03 | 0.03 | 1873 | 0.65 | 150.1591 | 97.6034 | 10.2 | 7.53 | 22.0323 | Y |  | 5
18 | NF | NF | NF | 0.03 | 0.02 | NF | 0.03 | 1861 | 0.65 | 151.1274 | 98.2328 | 9.7 | 7.57 | 23.0965 | Y |  | 5
19 | NF | NF | 0.03 | 0.02 | 0.02 | 0.03 | 0.08 | 1883 | 0.67 | 149.3617 | 100.0723 | 10 | 7.8 | 24.6191 | Y |  | 5
20 | NF | NF | NF | NF | 0.02 | 0.02 | 0.03 | 1867 | 0.65 | 150.6417 | 97.9171 | 11.3 | 7.38 | 19.4542 | Y |  | 5
21 | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF |  | 5
22 | NF | 0.03 | 0.02 | 0.02 | 0.03 | 0.02 | 0.04 | 1896 | 0.6 | 148.3376 | 89.0025 | 10.4 | 7.57 | 21.9273 | Y |  | 5
23 | 0.02 | 0.02 | NF | NF | NF | NF | 0.02 | 1828 | 0.71 | 153.8556 | 109.2375 | 10.6 | 7.58 | 21.9876 | Y |  | 5
24 | NF | NF | 0.02 | 0.02 | 0.02 | NF | 0.02 | 1875 | 0.64 | 149.9989 | 95.9993 | 10.8 | 7.58 | 21.529 | Y |  | 5
25 | NF | NF | NF | 0.02 | NF | NF | 0.02 | 1875 | 0.66 | 149.9989 | 98.9993 | 10.3 | 7.38 | 20.7903 | Y |  | 5
26 | NF | 0.02 | 0.02 | 0.02 | 0.02 | NF | 0.02 | 1864 | 0.68 | 150.8841 | 102.6012 | 10.3 | 7.7 | 23.3183 | Y |  | 5
27 | NF | NF | 0.02 | 0.02 | 0.02 | NF | 0.03 | 1895 | 0.66 | 148.4158 | 97.9544 | 10.2 | 7.66 | 23.0914 | Y |  | 5
28 | NF | NF | NF | 0.02 | 0.02 | 0.02 | 0.02 | 1880 | 0.66 | 149.6 | 98.736 | 10.2 | 7.59 | 22.5281 | Y |  | 5
29 | NF | NF | 0.02 | NF | NF | NF | 0.03 | 1852 | 0.64 | 151.8618 | 97.1915 | 10.3 | 7.47 | 21.4073 | Y |  | 5
30 | [9 empty] | #DIV/0! | #DIV/0! |  |  | 4.185 | #DIV/0! |  | 5
31 | [9 empty] | #DIV/0! | #DIV/0! |  |  | 4.185 | #DIV/0! |  | 5
AVG. | 0.02 | 0.0225 | 0.021818 | 0.02125 | 0.021739 | 0.022143 | 0.0325 | 1872.0357 | 0.67214 | #DIV/0! | #DIV/0! | 10.5286 | 7.6314 | 21.2472
MAX. | 0.02 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.08 | 1896
MIN | Conventional Filtration | [7 empty] | 0.6
95% of 4 hr turbidity readings </= 0.3 NTU? Yes | [5 empty] | All turbidity readings < IFE2 triggers? Yes |  |  |  |  | CT's met everyday? Yes |  |  | All Cl2 Residual at entry point
All the 4 hr turbidity readings </= 1.0 NTU? Yes | [13 empty] | >/= 0.2 mg/L Yes
1 Including continuous turbidity data, if applicable, for optimization recording purposes. Compliance values in Columns "12am through 8pm" may not correspond to continuous readings maximum.
2 IFE = Individual Filter Effluent | [7 empty] | Name (Printed): | Jaegar Howatt |  |  | Signature:
3 If Cl2 at entry point <0.2 mg/l, or CT not met, notify DWP by end of next business day. | [7 empty] | Operator Cert. #: | T-448091 |  |  | Date: |  | 2024-05-15
4 NF=No Flow | [7 empty] | Phone #: | 541-570-7561