## Sheet1
OHA - Drinking Water Program - Turbidity Monitoring Report Form County: Linn Conventional Filtration
Sweet Home, City of |  |  |  | I.D. # OR4100851 |  |  | WTP: WTP-B |  | Month of | 2024-03-01 |  |  |  | Required Log inactivation: |  | 0.5
| TURBIDITY | [5 empty] | Highest | Peak Hourly | Min.Cl2 Res. | CONTACT | ACTUAL | TEMP |  | REQ. | CT | log *
| 12AM | 4AM | 8AM | NOON | 4PM | 8PM | Reading of Day 1 | Demand Flow | at 1st user | TIME | (CT) |  | pH | CT | MET? | inacti-
DATE | NTU | NTU | NTU | NTU | NTU | NTU | (NTU) | (gpm) | Mg/L (C)3 | MIN. (T) | C X T | Co |  | Formula | Y / N | vation
1 | NF | 0.02 | 0.02 | 0.02 | 0.02 | NF | 0.02 | 1857 | 0.64 | 151.4529 | 96.9298 | 9.6 | 7.46 | 22.3397 | Y |  | 5
2 | NF | NF | NF | 0.02 | 0.02 | 0.03 | 0.03 | 1870 | 0.61 | 150.4 | 91.744 | 11.7 | 7.62 | 20.5107 | Y |  | 5
3 | 0.02 | NF | NF | 0.02 | NF | NF | 0.03 | 1892 | 0.59 | 148.6512 | 87.7042 | 9.5 | 7.7 | 24.3418 | Y |  | 5
4 | NF | NF | 0.03 | 0.02 | 0.02 | NF | 0.03 | 1860 | 0.57 | 151.2086 | 86.1889 | 10.1 | 7.71 | 23.419 | Y |  | 5
5 | NF | NF | NF | 0.02 | 0.02 | 0.02 | 0.05 | 1881 | 0.51 | 149.5205 | 76.2554 | 9.6 | 7.72 | 24.1312 | Y |  | 5
6 | 0.02 | NF | NF | 0.04 | 0.02 | 0.02 | 0.2 | 1883 | 0.48 | 149.3617 | 71.6936 | 10.8 | 7.46 | 20.277 | Y |  | 5
7 | NF | NF | NF | 0.02 | NF | NF | 0.12 | 1859 | 0.76 | 151.2899 | 114.9804 | 10.2 | 7.45 | 21.6894 | Y |  | 5
8 | NF | NF | 0.02 | 0.02 | 0.02 | NF | 0.02 | 1868 | 0.77 | 150.561 | 115.932 | 9.6 | 7.39 | 22.1189 | Y |  | 5
9 | NF | NF | NF | 0.02 | 0.02 | NF | 0.03 | 1872 | 0.77 | 150.2393 | 115.6843 | 10.3 | 7.65 | 23.1452 | Y |  | 5
10 | NF | NF | 0.02 | 0.02 | NF | NF | 0.02 | 1876 | 0.74 | 149.919 | 110.94 | 9.5 | 7.75 | 25.2071 | Y |  | 5
11 | NF | 0.02 | 0.02 | 0.02 | 0.03 | 0.02 | 0.15 | 1869 | 0.75 | 150.4805 | 112.8604 | 9.8 | 7.73 | 24.56 | Y |  | 5
12 | 0.02 | NF | NF | NF | NF | 0.02 | 0.03 | 1882 | 0.74 | 149.441 | 110.5864 | 9.5 | 7.73 | 25.0282 | Y |  | 5
13 | 0.023 | NF | NF | NF | 0.03 | 0.02 | 0.03 | 1877 | 0.76 | 149.8391 | 113.8777 | 11 | 7.49 | 20.8687 | Y |  | 5
14 | NF | NF | NF | 0.02 | 0.02 | NF | 0.02 | 1873 | 0.76 | 150.1591 | 114.1209 | 10.3 | 7.48 | 21.7751 | Y |  | 5
15 | NF | NF | NF | 0.02 | NF | NF | 0.03 | 1869 | 0.76 | 150.4805 | 114.3652 | 10.1 | 7.64 | 23.345 | Y |  | 5
16 | NF | NF | 0.03 | 0.02 | 0.02 | 0.02 | 0.03 | 1915 | 0.72 | 146.8658 | 105.7434 | 10.5 | 7.67 | 22.8722 | Y |  | 5
17 | 0.02 | NF | 0.02 | NF | NF | NF | 0.02 | 1839 | 0.76 | 152.9353 | 116.2308 | 10.5 | 7.6 | 22.4159 | Y |  | 5
18 | NF | NF | 0.02 | 0.02 | 0.02 | 0.02 | 0.03 | 1878 | 0.75 | 149.7593 | 112.3195 | 10.5 | 7.82 | 24.2018 | Y |  | 5
19 | NF | NF | NF | 0.02 | 0.02 | NF | 0.04 | 1869 | 0.74 | 150.4805 | 111.3555 | 11.5 | 7.56 | 20.6493 | Y |  | 5
20 | NF | NF | NF | 0.02 | NF | NF | 0.03 | 1873 | 0.76 | 150.1591 | 114.1209 | 13.5 | 7.68 | 18.8381 | Y |  | 5
21 | NF | NF | 0.02 | 0.02 | 0.02 | NF | 0.03 | 1869 | 0.74 | 150.4805 | 111.3555 | 11.2 | 7.56 | 21.0596 | Y |  | 5
22 | NF | NF | NF | 0.02 | 0.02 | 0.02 | 0.03 | 1881 | 0.7 | 149.5205 | 104.6643 | 13.2 | 7.88 | 20.5464 | Y |  | 5
23 | 0.02 | NF | NF | NF | NF | NF | 0.04 | 1852 | 0.78 | 151.8618 | 118.4522 | 13.6 | 7.61 | 18.2777 | Y |  | 5
24 | NF | NF | NF | 0.02 | 0.02 | 0.02 | 0.03 | 1869 | 0.73 | 150.4805 | 109.8507 | 11.6 | 7.81 | 22.3681 | Y |  | 5
25 | 0.02 | NF | NF | 0.02 | 0.02 | NF | 0.02 | 1875 | 0.76 | 149.9989 | 113.9992 | 11.3 | 7.75 | 22.4149 | Y |  | 5
26 | NF | NF | 0.02 | 0.02 | 0.02 | NF | 0.04 | 1864 | 0.73 | 150.8841 | 110.1454 | 10.7 | 7.75 | 23.2442 | Y |  | 5
27 | NF | NF | 0.02 | 0.02 | 0.02 | NF | 0.03 | 1873 | 0.76 | 150.1591 | 114.1209 | 11.6 | 7.61 | 20.9228 | Y |  | 5
28 | NF | NF | NF | NF | 0.02 | 0.02 | 0.03 | 1881 | 0.6 | 149.5205 | 89.7123 | 12.3 | 7.65 | 19.9069 | Y |  | 5
29 | 0.02 | NF | NF | NF | NF | NF | 0.02 | NF | NF | NF | NF | NF | NF | NF | NF |  | 5
30 | NF | NF | NF | 0.02 | 0.05 | 0.03 | 0.05 | 1880 | 0.67 | 149.6 | 100.232 | 11.2 | 7.82 | 22.8929 | Y |  | 5
31 | 0.02 | 0.03 | NF | 0.03 | 0.03 | 0.03 | 0.04 | 1912 | 0.66 | 147.0962 | 97.0835 | 10.3 | 7.5 | 21.6826 | Y |  | 5
AVG. | 0.020333 | 0.023333 | 0.021818 | 0.0212 | 0.022727 | 0.022308 | 0.042581 | 1873.9333 | 0.70233 | 150.0935 | 105.4416 | 10.8367 | 7.6417 | 22.1684
MAX. | 0.023 | 0.03 | 0.03 | 0.04 | 0.05 | 0.03 | 0.2 | 1915
MIN | Conventional Filtration | [7 empty] | 0.48
95% of 4 hr turbidity readings </= 0.3 NTU? Yes | [5 empty] | All turbidity readings < IFE2 triggers? Yes |  |  |  |  | CT's met everyday? Yes |  |  | All Cl2 Residual at entry point
All the 4 hr turbidity readings </= 1.0 NTU? Yes | [13 empty] | >/= 0.2 mg/L Yes
1 Including continuous turbidity data, if applicable, for optimization recording purposes. Compliance values in Columns "12am through 8pm" may not correspond to continuous readings maximum.
2 IFE = Individual Filter Effluent | [7 empty] | Name (Printed): | Jaegar Howatt |  |  | Signature:
3 If Cl2 at entry point <0.2 mg/l, or CT not met, notify DWP by end of next business day. | [7 empty] | Operator Cert. #: | T-448091 |  |  | Date: |  | 2024-05-15
4 NF=No Flow | [7 empty] | Phone #: | 541-570-7561