## Sheet1
OHA - Drinking Water Program - Turbidity Monitoring Report Form County: Linn Conventional Filtration
Sweet Home, City of |  |  |  | I.D. # OR4100851 |  |  | WTP: WTP-B |  | Month of | 2024-05-01 |  |  |  | Required Log inactivation: |  | 0.5
| TURBIDITY | [5 empty] | Highest | Peak Hourly | Min.Cl2 Res. | CONTACT | ACTUAL | TEMP |  | REQ. | CT | log *
| 12AM | 4AM | 8AM | NOON | 4PM | 8PM | Reading of Day 1 | Demand Flow | at 1st user | TIME | (CT) |  | pH | CT | MET? | inacti-
DATE | NTU | NTU | NTU | NTU | NTU | NTU | (NTU) | (gpm) | Mg/L (C)3 | MIN. (T) | C X T | Co |  | Formula | Y / N | vation
1 | 0.03 | NF | NF | NF | 0.03 | 0.03 | 0.03 | 1756 | 0.63 | 160.164 | 100.9033 | 13.4 | 7.46 | 17.2283 | Y |  | 5
2 | NF | NF | NF | NF | 0.03 | 0.03 | 0.03 | 1753 | 0.66 | 160.4381 | 105.8892 | 12.3 | 7.9 | 21.8713 | Y |  | 5
3 | 0.03 | NF | NF | 0.03 | 0.05 | NF | 0.05 | 1763 | 0.66 | 159.5281 | 105.2885 | 13.4 | 7.47 | 17.3511 | Y |  | 5
4 | NF | NF | NF | NF | 0.03 | 0.03 | 0.04 | 1760 | 0.62 | 159.8 | 99.076 | 12.2 | 7.46 | 18.8023 | Y |  | 5
5 | 0.03 | 0.03 | 0.03 | NF | NF | NF | 0.03 | 1762 | 0.68 | 159.6186 | 108.5407 | 12 | 7.5 | 19.4426 | Y |  | 5
6 | NF | 0.03 | 0.03 | 0.03 | NF | NF | 0.07 | 1736 | 0.63 | 162.0092 | 102.0658 | 11.6 | 7.65 | 20.9098 | Y |  | 5
7 | NF | NF | NF | NF | 0.03 | 0.03 | 0.08 | 1769 | 0.56 | 158.987 | 89.0327 | 12.2 | 7.53 | 19.1347 | Y |  | 5
8 | 0.02 | NF | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 1766 | 0.67 | 159.2571 | 106.7022 | 11.5 | 7.75 | 21.897 | Y |  | 5
9 | NF | NF | NF | 0.02 | 0.02 | NF | 0.04 | 1735 | 0.67 | 162.1026 | 108.6087 | 12.3 | 7.77 | 20.9207 | Y |  | 5
10 | NF | NF | NF | NF | 0.02 | 0.02 | 0.04 | 1768 | 0.6 | 159.0769 | 95.4462 | 13.5 | 7.66 | 18.3633 | Y |  | 5
11 | 0.02 | 0.02 | 0.02 | 0.03 | 0.02 | NF | 0.03 | 1737 | 0.71 | 161.9159 | 114.9603 | 13.8 | 7.7 | 18.498 | Y |  | 5
12 | NF | NF | NF | 0.02 | 0.02 | NF | 0.03 | 1775 | 0.71 | 158.4496 | 112.4992 | 14.2 | 7.58 | 17.2318 | Y |  | 5
13 | NF | NF | 0.02 | NF | 0.02 | 0.02 | 0.02 | 1779 | 0.76 | 158.0933 | 120.1509 | 13.6 | 7.71 | 18.9216 | Y |  | 5
14 | NF | NF | NF | 0.02 | 0.02 | NF | 0.03 | 1750 | 0.72 | 160.7131 | 115.7135 | 13.2 | 7.58 | 18.4374 | Y |  | 5
15 | NF | NF | NF | 0.02 | 0.02 | 0.02 | 0.03 | 1774 | 0.72 | 158.5389 | 114.148 | 15.2 | 7.65 | 16.5636 | Y |  | 5
16 | 0.02 | 0.02 | NF | 0.02 | 0.02 | NF | 0.04 | 1767 | 0.75 | 159.1669 | 119.3752 | 15.3 | 7.85 | 17.7765 | Y |  | 5
17 | NF | NF | NF | 0.03 | 0.03 | 0.03 | 0.03 | 1765 | 0.73 | 159.3473 | 116.3235 | 14.6 | 7.76 | 17.9738 | Y |  | 5
18 | 0.03 | NF | NF | 0.03 | 0.03 | NF | 0.04 | 1758 | 0.75 | 159.9818 | 119.9863 | 14.2 | 7.7 | 18.0948 | Y |  | 5
19 | NF | NF | NF | 0.02 | 0.02 | NF | 0.03 | 1773 | 0.75 | 158.6283 | 118.9712 | 13.1 | 7.48 | 17.9488 | Y |  | 5
20 | NF | NF | 0.03 | 0.02 | 0.03 | 0.03 | 0.03 | 1761 | 0.71 | 159.7093 | 113.3936 | 12.7 | 7.39 | 17.7492 | Y |  | 5
21 | NF | NF | NF | 0.03 | 0.02 | 0.03 | 0.05 | 1753 | 0.69 | 160.4381 | 110.7023 | 12.5 | 7.37 | 17.814 | Y |  | 5
22 | 0.03 | NF | NF | 0.02 | 0.02 | NF | 0.04 | 1759 | 0.7 | 159.8908 | 111.9236 | 12.7 | 7.36 | 17.5337 | Y |  | 5
23 | NF | NF | NF | 0.02 | 0.03 | 0.02 | 0.04 | 1767 | 0.66 | 159.1669 | 105.0502 | 12 | 7.22 | 17.616 | Y |  | 5
24 | 0.03 | NF | NF | NF | 0.021 | NF | 0.03 | 1751 | 0.69 | 160.6214 | 110.8287 | 12.8 | 7.54 | 18.5932 | Y |  | 5
25 | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF |  | 5
26 | NF | NF | NF | 0.03 | 0.02 | 0.02 | 0.04 | 1797 | 0.6 | 156.5097 | 93.9058 | 12.4 | 7.53 | 18.9722 | Y |  | 5
27 | 0.02 | 0.02 | 0.02 | 0.03 | 0.02 | 0.02 | 0.03 | 1778 | 0.68 | 158.1822 | 107.5639 | 11.5 | 7.43 | 19.6039 | Y |  | 5
28 | 0.03 | NF | 0.03 | 0.02 | 0.02 | 0.02 | 0.03 | 1772 | 0.69 | 158.7178 | 109.5153 | 11.5 | 7.52 | 20.2496 | Y |  | 5
29 | 0.02 | NF | NF | 0.03 | 0.02 | NF | 0.03 | 1753 | 0.68 | 160.4381 | 109.0979 | 11.8 | 7.62 | 20.5374 | Y |  | 5
30 | NF | NF | NF | NF | 0.02 | 0.02 | 0.03 | 1774 | 0.65 | 158.5389 | 103.0503 | 11.8 | 7.71 | 21.1222 | Y |  | 5
31 | 0.03 | 0.02 | 0.02 | NF | 0.03 | 0.02 | 0.03 | 1747 | 0.66 | 160.9891 | 106.2528 | 11 | 7.41 | 20.0684 | Y |  | 5
AVG. | 0.026154 | 0.023333 | 0.025556 | 0.025 | 0.024679 | 0.024706 | 0.037333 | 1761.9333 | 0.67967 | 159.634 | 108.4989 | 12.81 | 7.5753 | 18.9076
MAX. | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.03 | 0.08 | 1797
MIN | Conventional Filtration | [7 empty] | 0.56
95% of 4 hr turbidity readings </= 0.3 NTU? Y | [5 empty] | All turbidity readings < IFE2 triggers? Y |  |  |  |  | CT's met everyday? Yes |  |  | All Cl2 Residual at entry point
All the 4 hr turbidity readings </= 1.0 NTU? Y | [13 empty] | >/= 0.2 mg/L Yes
1 Including continuous turbidity data, if applicable, for optimization recording purposes. Compliance values in Columns "12am through 8pm" may not correspond to continuous readings maximum.
2 IFE = Individual Filter Effluent | [7 empty] | Name (Printed): | Jaegar Howatt |  |  | Signature:
3 If Cl2 at entry point <0.2 mg/l, or CT not met, notify DWP by end of next business day. | [7 empty] | Operator Cert. #: | T-448091 |  |  | Date: | 2024-06-01
4 NF=No Flow | [7 empty] | Phone #: | 541-570-7561