## Sheet1
OHA - Drinking Water Program - Turbidity Monitoring Report Form County: Linn Conventional Filtration
Sweet Home, City of |  |  |  | I.D. # OR4100851 |  |  | WTP: WTP-B |  | Month of | 2024-06-01 |  |  |  | Required Log inactivation: |  | 0.5
| TURBIDITY | [5 empty] | Highest | Peak Hourly | Min.Cl2 Res. | CONTACT | ACTUAL | TEMP |  | REQ. | CT | log *
| 12AM | 4AM | 8AM | NOON | 4PM | 8PM | Reading of Day 1 | Demand Flow | at 1st user | TIME | (CT) |  | pH | CT | MET? | inacti-
DATE | NTU | NTU | NTU | NTU | NTU | NTU | (NTU) | (gpm) | Mg/L (C)3 | MIN. (T) | C X T | Co |  | Formula | Y / N | vation
1 | NF | 0.02 | NF | NF | NF | 0.02 | 0.03 | 1775 | 0.67 | 158.4496 | 106.1612 | 13.5 | 7.55 | 17.7732 | Y |  | 5
2 | 0.02 | NF | NF | 0.02 | 0.02 | 0.02 | 0.04 | 1759 | 0.71 | 159.8908 | 113.5225 | 11.8 | 7.64 | 20.751 | Y |  | 5
3 | NF | NF | NF | 0.02 | 0.02 | 0.02 | 0.03 | 1763 | 0.67 | 159.5281 | 106.8838 | 11.5 | 7.32 | 18.8506 | Y |  | 5
4 | NF | NF | 0.02 | 0.03 | 0.02 | NF | 0.03 | 1757 | 0.65 | 160.0729 | 104.0474 | 11.5 | 7.46 | 19.743 | Y |  | 5
5 | NF | NF | NF | 0.02 | 0.02 | NF | 0.03 | 1760 | 0.69 | 159.8 | 110.262 | 11.4 | 7.14 | 17.8728 | Y |  | 5
6 | NF | NF | 0.03 | 0.02 | 0.02 | NF | 0.03 | 1774 | 0.71 | 158.5389 | 112.5626 | 10.9 | 7.23 | 19.0829 | Y |  | 5
7 | NF | NF | NF | 0.03 | 0.03 | 0.03 | 0.07 | 1788 | 0.66 | 157.2975 | 103.8164 | 11.9 | 7.58 | 20.0762 | Y |  | 5
8 | 0.07 | 0.03 | 0.03 | 0.03 | 0.02 | NF | 0.09 | 1767 | 0.67 | 159.1669 | 106.6419 | 12.4 | 7.72 | 20.4244 | Y |  | 5
9 | NF | NF | NF | 0.03 | 0.02 | 0.02 | 0.07 | 1773 | 0.67 | 158.6283 | 106.281 | 12.6 | 7.36 | 17.5907 | Y |  | 5
10 | 0.03 | NF | NF | 0.03 | 0.03 | NF | 0.03 | 1763 | 0.67 | 159.5281 | 106.8838 | 13.8 | 7.34 | 16.1204 | Y |  | 5
11 | NF | NF | 0.03 | 0.03 | 0.03 | 0.03 | 0.04 | 1778 | 0.74 | 158.1822 | 117.0548 | 13.7 | 7.69 | 18.616 | Y |  | 5
12 | NF | NF | NF | 0.03 | 0.03 | 0.03 | 0.03 | 1782 | 0.7 | 157.8272 | 110.479 | 14.5 | 7.69 | 17.572 | Y |  | 5
13 | NF | NF | NF | 0.03 | 0.03 | 0.02 | 0.03 | 1758 | 0.69 | 159.9818 | 110.3874 | 13.8 | 7.23 | 15.5122 | Y |  | 5
14 | 0.03 | 0.02 | 0.03 | NF | 0.03 | 0.02 | 0.04 | 1766 | 0.67 | 159.2571 | 106.7022 | 13.2 | 7.6 | 18.4689 | Y |  | 5
15 | 0.03 | 0.02 | 0.02 | NF | 0.03 | 0.03 | 0.04 | 1771 | 0.67 | 158.8075 | 106.401 | 14 | 7.58 | 17.3835 | Y |  | 5
16 | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF |  | 5
17 | NF | NF | NF | 0.02 | 0.02 | 0.02 | 0.04 | 1788 | 0.69 | 157.2975 | 108.5353 | 13.9 | 7.45 | 16.7165 | Y |  | 5
18 | 0.02 | NF | 0.03 | 0.03 | 0.02 | 0.02 | 0.1 | 1791 | 0.67 | 157.0341 | 105.2128 | 12.8 | 7.33 | 17.1669 | Y |  | 5
19 | 0.03 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03 | 1819 | 0.77 | 154.6168 | 119.055 | 12.8 | 7.48 | 18.3519 | Y |  | 5
20 | 0.02 | 0.02 | NF | NF | 0.02 | 0.02 | 0.03 | 1768 | 0.71 | 159.0769 | 112.9446 | 13.4 | 7.21 | 15.8501 | Y |  | 5
21 | 0.02 | NF | NF | NF | 0.02 | 0.02 | 0.03 | 1784 | 0.66 | 157.6502 | 104.0491 | 13.9 | 7.64 | 17.8713 | Y |  | 5
22 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | NF | 0.19 | 1774 | 0.6 | 158.5389 | 95.1233 | 13.5 | 7.29 | 16.0162 | Y |  | 5
23 | NF | NF | NF | 0.02 | 0.02 | 0.02 | 0.03 | 1793 | 0.65 | 156.8589 | 101.9583 | 12.5 | 7.43 | 18.1305 | Y |  | 5
24 | 0.02 | 0.03 | 0.03 | NF | NF | 0.02 | 0.03 | 1785 | 0.64 | 157.5619 | 100.8396 | 12.4 | 7.18 | 16.9007 | Y |  | 5
25 | 0.03 | 0.02 | 0.03 | 0.03 | 0.02 | NF | 0.03 | 1770 | 0.65 | 158.8972 | 103.2832 | 12.3 | 7.4 | 18.3597 | Y |  | 5
26 | NF | 0.03 | 0.02 | 0.03 | NF | NF | 0.03 | 1776 | 0.63 | 158.3604 | 99.767 | 12.5 | 7.43 | 18.0894 | Y |  | 5
27 | NF | NF | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 1787 | 0.61 | 157.3856 | 96.0052 | 12.2 | 7.49 | 18.9771 | Y |  | 5
28 | 0.025 | NF | NF | 0.026 | 0.025 | NF | 0.032 | 1768 | 0.64 | 159.0769 | 101.8092 | 12.1 | 7.61 | 19.9789 | Y |  | 5
29 | NF | NF | NF | 0.03 | 0.02 | 0.03 | 0.03 | 1787 | 0.63 | 157.3856 | 99.1529 | 12.5 | 7.46 | 18.2908 | Y |  | 5
30 | NF | NF | NF | 0.03 | 0.03 | 0.03 | 0.03 | 1793 | 0.6 | 156.8589 | 94.1153 | 12.6 | 7.46 | 18.1079 | Y |  | 5
31 | [9 empty] | #DIV/0! | #DIV/0! |  |  | 4.185 | #DIV/0! |  | 5
AVG. | 0.028077 | 0.023 | 0.026154 | 0.026348 | 0.023654 | 0.0235 | 0.044552 | 1776.4483 | 0.66862 | #DIV/0! | #DIV/0! | 12.7552 | 7.4479 | 17.6277
MAX. | 0.07 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.19 | 1819
MIN | Conventional Filtration | [7 empty] | 0.6
95% of 4 hr turbidity readings </= 0.3 NTU? Y | [5 empty] | All turbidity readings < IFE2 triggers? Y |  |  |  |  | CT's met everyday? Yes |  |  | All Cl2 Residual at entry point
All the 4 hr turbidity readings </= 1.0 NTU? Y | [13 empty] | >/= 0.2 mg/L Yes
1 Including continuous turbidity data, if applicable, for optimization recording purposes. Compliance values in Columns "12am through 8pm" may not correspond to continuous readings maximum.
2 IFE = Individual Filter Effluent | [7 empty] | Name (Printed): | Jaegar Howatt |  |  | Signature:
3 If Cl2 at entry point <0.2 mg/l, or CT not met, notify DWP by end of next business day. | [7 empty] | Operator Cert. #: | T-448091 |  |  | Date: | 2024-07-03
4 NF=No Flow | [7 empty] | Phone #: | 541570-7561