## Sheet1
OHA - Drinking Water Program - Turbidity Monitoring Report Form County: Linn Conventional Filtration
Sweet Home, City of |  |  |  | I.D. # OR4100851 |  |  | WTP: WTP-B |  | Month of | 2024-07-01 |  |  |  | Required Log inactivation: |  | 0.5
| TURBIDITY | [5 empty] | Highest | Peak Hourly | Min.Cl2 Res. | CONTACT | ACTUAL | TEMP |  | REQ. | CT | log *
| 12AM | 4AM | 8AM | NOON | 4PM | 8PM | Reading of Day 1 | Demand Flow | at 1st user | TIME | (CT) |  | pH | CT | MET? | inacti-
DATE | NTU | NTU | NTU | NTU | NTU | NTU | (NTU) | (gpm) | Mg/L (C)3 | MIN. (T) | C X T | Co |  | Formula | Y / N | vation
1 | 0.03 | 0.03 | 0.03 | 0.03 | NF | NF | 0.03 | 1770 | 0.65 | 158.8972 | 103.2832 | 12.5 | 7.32 | 17.4088 | Y |  | 5
2 | NF | NF | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 1780 | 0.65 | 158.0045 | 102.7029 | 12.8 | 7.48 | 18.1036 | Y |  | 5
3 | 0.03 | 0.03 | NF | NF | NF | 0.03 | 0.03 | 1804 | 0.62 | 155.9024 | 96.6595 | 14.6 | 7.65 | 17.0437 | Y |  | 5
4 | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF |  |  | 5
5 | NF | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04 | 1811 | 0.56 | 155.2998 | 86.9679 | 12.9 | 7.37 | 17.092 | Y |  | 5
6 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 1818 | 0.67 | 154.7019 | 103.6503 | 12.8 | 7.63 | 19.1771 | Y |  | 5
7 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04 | 1789 | 0.66 | 157.2096 | 103.7583 | 13 | 7.42 | 17.4929 | Y |  | 5
8 | 0.04 | NF | NF | 0.03 | 0.07 | 0.03 | 0.08 | 1794 | 0.62 | 156.7715 | 97.1983 | 14.2 | 8.07 | 20.4359 | Y |  | 5
9 | NF | NF | NF | NF | 0.03 | 0.03 | 0.06 | 1796 | 0.33 | 156.5969 | 51.677 | 14 | 7.53 | 16.4181 | Y |  | 5
10 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 1792 | 0.85 | 156.9464 | 133.4045 | 12.9 | 7.26 | 16.9609 | Y |  | 5
11 | 0.03 | 0.03 | NF | 0.03 | 0.03 | 0.03 | 0.03 | 1787 | 0.85 | 157.3856 | 133.7777 | 12.9 | 7.39 | 17.7954 | Y |  | 5
12 | 0.03 | NF | NF | 0.03 | 0.03 | 0.03 | 0.03 | 1786 | 0.78 | 157.4737 | 122.8295 | 15 | 7.69 | 17.1523 | Y |  | 5
13 | 0.03 | 0.03 | 0.03 | 0.03 | NF | NF | 0.05 | 1768 | 0.79 | 159.0769 | 125.6708 | 13.9 | 7.57 | 17.6742 | Y |  | 5
14 | 0.03 | 0.03 | 0.03 | NF | NF | 0.03 | 0.03 | 1792 | 0.8 | 156.9464 | 125.5571 | 12.9 | 7.57 | 18.91 | Y |  | 5
15 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | NF | 0.03 | 1798 | 0.81 | 156.4227 | 126.7024 | 13.3 | 7.27 | 16.501 | Y |  | 5
16 | NF | 0.03 | 0.03 | 0.03 | 0.03 | NF | 0.04 | 1781 | 0.78 | 157.9158 | 123.1743 | 13.8 | 7.43 | 16.876 | Y |  | 5
17 | NF | 0.03 | 0.03 | 0.03 | 0.03 | NF | 0.03 | 1777 | 0.76 | 158.2712 | 120.2861 | 14.1 | 7.6 | 17.575 | Y |  | 5
18 | NF | 0.03 | 0.03 | 0.03 | NF | NF | 0.04 | 1808 | 0.8 | 155.5575 | 124.446 | 13 | 7.67 | 19.4904 | Y |  | 5
19 | NF | NF | NF | 0.02 | 0.03 | 0.03 | 0.04 | 1796 | 0.76 | 156.5969 | 119.0136 | 13.3 | 7.53 | 18.0622 | Y |  | 5
20 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04 | 1791 | 0.78 | 157.0341 | 122.4866 | 12.7 | 7.51 | 18.701 | Y |  | 5
21 | 0.03 | 0.04 | NF | 0.03 | 0.03 | 0.03 | 0.04 | 1782 | 0.79 | 157.8272 | 124.6835 | 13.2 | 7.31 | 16.8206 | Y |  | 5
22 | 0.02 | NF | NF | 0.03 | 0.03 | 0.03 | 0.04 | 1789 | 0.77 | 157.2096 | 121.0514 | 13.5 | 7.54 | 17.9099 | Y |  | 5
23 | 0.03 | NF | NF | 0.03 | 0.03 | 0.02 | 0.04 | 1775 | 0.75 | 158.4496 | 118.8372 | 13.3 | 7.49 | 17.7772 | Y |  | 5
24 | 0.03 | NF | 0.03 | 0.03 | 0.03 | NF | 0.03 | 1793 | 0.74 | 156.8589 | 116.0756 | 13.3 | 7.56 | 18.2219 | Y |  | 5
25 | NF | NF | NF | 0.03 | 0.07 | 0.03 | 0.07 | 1792 | 0.75 | 156.9464 | 117.7098 | 13.3 | 7.5 | 17.843 | Y |  | 5
26 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | NF | 0.03 | 1770 | 0.74 | 158.8972 | 117.5839 | 12.3 | 7.53 | 19.3954 | Y |  | 5
27 | NF | 0.03 | 0.03 | 0.03 | 0.03 | NF | 0.03 | 1764 | 0.74 | 159.4376 | 117.9839 | 12.5 | 7.47 | 18.589 | Y |  | 5
28 | 0.03 | 0.03 | 0.03 | 0.03 | NF | NF | 0.04 | 1773 | 0.72 | 158.6283 | 114.2124 | 12.9 | 7.51 | 18.329 | Y |  | 5
29 | 0.03 | 0.03 | 0.03 | NF | NF | NF | 0.03 | 1765 | 0.72 | 159.3473 | 114.7301 | 12.9 | 7.49 | 18.1942 | Y |  | 5
30 | 0.03 | 0.03 | 0.03 | NF | NF | 0.03 | 0.04 | 1784 | 0.7 | 157.6502 | 110.3552 | 12.8 | 7.49 | 18.274 | Y |  | 5
31 | 0.03 | 0.05 | 0.05 | NF | NF | NF | 0.05 | 1756 | 0.68 | 160.164 | 108.9115 | 14.4 | 7.57 | 16.8836 | Y |  | 5
AVG. | 0.03 | 0.031429 | 0.031 | 0.029583 | 0.03381 | 0.029444 | 0.039 | 1786.0333 | 0.72067 | 157.4809 | 113.5127 | 13.3 | 7.514 | 17.9036
MAX. | 0.04 | 0.05 | 0.05 | 0.03 | 0.07 | 0.03 | 0.08 | 1818
MIN | Conventional Filtration | [7 empty] | 0.33
95% of 4 hr turbidity readings </= 0.3 NTU? Y | [5 empty] | All turbidity readings < IFE2 triggers? Y |  |  |  |  | CT's met everyday? Yes |  |  | All Cl2 Residual at entry point
All the 4 hr turbidity readings </= 1.0 NTU? Y | [13 empty] | >/= 0.2 mg/L Yes
1 Including continuous turbidity data, if applicable, for optimization recording purposes. Compliance values in Columns "12am through 8pm" may not correspond to continuous readings maximum.
2 IFE = Individual Filter Effluent | [7 empty] | Name (Printed): | Jaegar Howatt |  |  | Signature:
3 If Cl2 at entry point <0.2 mg/l, or CT not met, notify DWP by end of next business day. | [7 empty] | Operator Cert. #: | T-448091 |  |  | Date: | 2024-08-01
4 NF=No Flow | [7 empty] | Phone #: | 541-570-7561