## Sheet1
OHA - Drinking Water Program - Turbidity Monitoring Report Form County: Linn Conventional Filtration
Sweet Home, City of |  |  |  | I.D. # OR4100851 |  |  | WTP: WTP-B |  | Month of | 2024-08-01 |  |  |  | Required Log inactivation: |  | 0.5
| TURBIDITY | [5 empty] | Highest | Peak Hourly | Min.Cl2 Res. | CONTACT | ACTUAL | TEMP |  | REQ. | CT | log *
| 12AM | 4AM | 8AM | NOON | 4PM | 8PM | Reading of Day 1 | Demand Flow | at 1st user | TIME | (CT) |  | pH | CT | MET? | inacti-
DATE | NTU | NTU | NTU | NTU | NTU | NTU | (NTU) | (gpm) | Mg/L (C)3 | MIN. (T) | C X T | Co |  | Formula | Y / N | vation
1 | NF | NF | NF | 0.03 | 0.03 | 0.04 | 0.04 | 1810 | 0.67 | 155.3856 | 104.1084 | 13.9 | 7.52 | 17.1158 | Y |  | 5
2 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04 | 1780 | 0.75 | 158.0045 | 118.5034 | 13.3 | 7.13 | 15.561 | Y |  | 5
3 | 0.03 | 0.03 | NF | 0.03 | 0.03 | NF | 0.1 | 1759 | 0.77 | 159.8908 | 123.116 | 14.5 | 7.34 | 15.5615 | Y |  | 5
4 | NF | 0.03 | 0.03 | 0.03 | NF | NF | 0.03 | 1800 | 0.76 | 156.2489 | 118.7492 | 13.2 | 7.36 | 17.0761 | Y |  | 5
5 | 0.03 | 0.03 | 0.03 | 0.03 | NF | NF | 0.03 | 1773 | 0.75 | 158.6283 | 118.9712 | 13.4 | 7.35 | 16.769 | Y |  | 5
6 | NF | NF | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 1802 | 0.74 | 156.0755 | 115.4958 | 13.4 | 7.3 | 16.443 | Y |  | 5
7 | 0.03 | 0.03 | 0.03 | 0.03 | NF | NF | 0.03 | 1803 | 0.76 | 155.9889 | 118.5516 | 13.6 | 7.3 | 16.2623 | Y |  | 5
8 | 0.03 | 0.03 | 0.03 | 0.03 | NF | 0.03 | 0.04 | 1780 | 0.76 | 158.0045 | 120.0834 | 14.5 | 7.47 | 16.3102 | Y |  | 5
9 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 1779 | 0.75 | 158.0933 | 118.57 | 13.9 | 7.49 | 17.0816 | Y |  | 5
10 | NF | NF | 0.03 | 0.03 | 0.03 | 0.02 | 0.03 | 1775 | 0.77 | 158.4496 | 122.0062 | 13 | 7.43 | 17.7783 | Y |  | 5
11 | 0.03 | NF | NF | 0.03 | 0.03 | 0.03 | 0.03 | 1775 | 0.74 | 158.4496 | 117.2527 | 13.3 | 7.48 | 17.6916 | Y |  | 5
12 | 0.03 | NF | NF | 0.03 | 0.03 | 0.03 | 0.04 | 1768 | 0.77 | 159.0769 | 122.4892 | 13.9 | 7.52 | 17.3114 | Y |  | 5
13 | 0.03 | NF | NF | 0.03 | 0.03 | 0.03 | 0.03 | 1763 | 0.74 | 159.5281 | 118.0508 | 13.6 | 7.59 | 18.0611 | Y |  | 5
14 | NF | NF | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 1771 | 0.75 | 158.8075 | 119.1056 | 12.4 | 7.59 | 19.6967 | Y |  | 5
15 | NF | NF | NF | 0.03 | 0.03 | 0.03 | 0.03 | 1761 | 0.75 | 159.7093 | 119.7819 | 13.6 | 7.57 | 17.9486 | Y |  | 5
16 | 0.03 | NF | NF | 0.03 | 0.02 | 0.03 | 0.04 | 1760 | 0.74 | 159.8 | 118.252 | 13.6 | 7.46 | 17.2144 | Y |  | 5
17 | NF | NF | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 1760 | 0.75 | 159.8 | 119.85 | 14.2 | 7.57 | 17.2465 | Y |  | 5
18 | 0.03 | NF | NF | 0.03 | 0.03 | 0.03 | 0.04 | 1767 | 0.73 | 159.1669 | 116.1919 | 14.2 | 7.44 | 16.3997 | Y |  | 5
19 | 0.03 | NF | NF | 0.03 | 0.03 | 0.03 | 0.03 | 1768 | 0.73 | 159.0769 | 116.1262 | 14.5 | 7.47 | 16.2546 | Y |  | 5
20 | NF | NF | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 1780 | 0.74 | 158.0045 | 116.9233 | 14.3 | 7.53 | 16.8615 | Y |  | 5
21 | NF | NF | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 1805 | 0.75 | 155.8161 | 116.862 | 14.6 | 7.61 | 17.0436 | Y |  | 5
22 | 0.03 | NF | NF | NF | 0.02 | 0.03 | 0.04 | 1770 | 0.62 | 158.8972 | 98.5162 | 14.5 | 7.77 | 17.9352 | Y |  | 5
23 | 0.03 | 0.03 | 0.03 | 0.02 | NF | 0.03 | 0.07 | 1736 | 0.58 | 162.0092 | 93.9653 | 15.4 | 7.55 | 15.5012 | Y |  | 5
24 | NF | 0.03 | 0.03 | NF | NF | NF | 0.03 | 1888 | 0.81 | 148.9661 | 120.6625 | 14.7 | 7.54 | 16.6108 | Y |  | 5
25 | 0.03 | 0.03 | 0.03 | 0.03 | NF | NF | 0.03 | 1889 | 0.82 | 148.8872 | 122.0875 | 14.5 | 7.44 | 16.2406 | Y |  | 5
26 | 0.03 | 0.03 | 0.03 | NF | NF | NF | 0.03 | 1890 | 0.8 | 148.8085 | 119.0468 | 13.6 | 7.43 | 17.141 | Y |  | 5
27 | 0.03 | 0.03 | 0.03 | NF | NF | NF | 0.04 | 1887 | 0.78 | 149.045 | 116.2551 | 14.1 | 7.43 | 16.5422 | Y |  | 5
28 | 0.03 | 0.03 | 0.03 | NF | NF | NF | 0.03 | 1886 | 0.71 | 149.1241 | 105.8781 | 12.7 | 7.4 | 17.8149 | Y |  | 5
29 | 0.03 | 0.03 | 0.03 | NF | NF | NF | 0.03 | 1883 | 0.78 | 149.3617 | 116.5021 | 14.4 | 7.4 | 16.0358 | Y |  | 5
30 | NF | NF | 0.02 | 0.03 | 0.03 | 0.03 | 0.05 | 1934 | 0.59 | 145.423 | 85.7995 | 15 | 7.43 | 15.2454 | Y |  | 5
31 | 0.03 | 0.03 | 0.02 | 0.03 | 0.03 | 0.03 | 0.03 | 1932 | 0.8 | 145.5735 | 116.4588 | 17.6 | 7.24 | 12.2262 | Y |  | 5
AVG. | 0.03 | 0.03 | 0.029048 | 0.0296 | 0.029 | 0.03 | 0.038065 | 1807.5484 | 0.74065 | 155.7452 | 115.2972 | 14.0452 | 7.4565 | 16.7413
MAX. | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04 | 0.1 | 1934
MIN | Conventional Filtration | [7 empty] | 0.58
95% of 4 hr turbidity readings </= 0.3 NTU? Y | [5 empty] | All turbidity readings < IFE2 triggers? Y |  |  |  |  | CT's met everyday? Yes |  |  | All Cl2 Residual at entry point
All the 4 hr turbidity readings </= 1.0 NTU? Y | [13 empty] | >/= 0.2 mg/L Yes
1 Including continuous turbidity data, if applicable, for optimization recording purposes. Compliance values in Columns "12am through 8pm" may not correspond to continuous readings maximum.
2 IFE = Individual Filter Effluent | [7 empty] | Name (Printed): | Jaegar Howatt |  |  | Signature:
3 If Cl2 at entry point <0.2 mg/l, or CT not met, notify DWP by end of next business day. | [7 empty] | Operator Cert. #: | T-448091 |  |  | Date: | 9-3-2.24
4 NF=No Flow | [7 empty] | Phone #: | 541-570-7561