## Sheet1
OHA - Drinking Water Program - Turbidity Monitoring Report Form County: Linn Conventional Filtration
Sweet Home, City of |  |  |  | I.D. # OR4100851 |  |  | WTP: WTP-B |  | Month of | 2024-09-01 |  |  |  | Required Log inactivation: |  | 0.5
| TURBIDITY | [5 empty] | Highest | Peak Hourly | Min.Cl2 Res. | CONTACT | ACTUAL | TEMP |  | REQ. | CT | log *
| 12AM | 4AM | 8AM | NOON | 4PM | 8PM | Reading of Day 1 | Demand Flow | at 1st user | TIME | (CT) |  | pH | CT | MET? | inacti-
DATE | NTU | NTU | NTU | NTU | NTU | NTU | (NTU) | (gpm) | Mg/L (C)3 | MIN. (T) | C X T | Co |  | Formula | Y / N | vation
1 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.02 | 0.03 | 1912 | 0.84 | 147.0962 | 123.5608 | 14.4 | 7.53 | 16.9411 | Y |  | 5
2 | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF |  | 5
3 | NF | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04 | 1939 | 0.78 | 145.048 | 113.1374 | 15.3 | 7.59 | 16.2026 | Y |  | 5
4 | 0.028 | 0.026 | 0.026 | 0.026 | 0.024 | 0.023 | 0.064 | 1892 | 0.82 | 148.6512 | 121.894 | 15.9 | 7.45 | 14.8475 | Y |  | 5
5 | 0.022 | 0.02 | 0.02 | 0.024 | 0.023 | NF | 0.024 | 1883 | 0.8 | 149.3617 | 119.4893 | 16.2 | 7.57 | 15.1806 | Y |  | 5
6 | NF | 0.025 | 0.022 | 0.021 | 0.019 | 0.025 | 0.044 | 1878 | 0.77 | 149.7593 | 115.3147 | 14.8 | 7.58 | 16.6705 | Y |  | 5
7 | NF | NF | NF | 0.03 | 0.02 | 0.03 | 0.03 | 1899 | 0.77 | 148.1032 | 114.0395 | 15.9 | 7.57 | 15.4347 | Y |  | 5
8 | 0.021 | NF | NF | 0.023 | 0.023 | 0.02 | 0.027 | 1896 | 0.78 | 148.3376 | 115.7033 | 16.21 | 7.52 | 14.8578 | Y |  | 5
9 | NF | NF | NF | 0.023 | 0.022 | 0.023 | 0.028 | 1895 | 0.78 | 148.4158 | 115.7643 | 14.1 | 7.55 | 17.2926 | Y |  | 5
10 | 0.023 | 0.022 | 0.022 | 0.02 | NF | NF | 0.023 | 1896 | 0.81 | 148.3376 | 120.1534 | 15.3 | 7.56 | 16.0784 | Y |  | 5
11 | NF | NF | NF | NF | 0.021 | 0.023 | 0.026 | 1913 | 0.74 | 147.0193 | 108.7943 | 14.6 | 7.57 | 16.7743 | Y |  | 5
12 | 0.022 | 0.02 | 0.02 | 0.02 | 0.14 | 0.17 | 0.18 | 1913 | 0.74 | 147.0193 | 108.7943 | 14.8 | 7.58 | 16.6137 | Y |  | 5
13 | 0.05 | 0.05 | 0.18 | NF | NF | 0.02 | 0.18 | 1883 | 0.7 | 149.3617 | 104.5532 | 15 | 7.31 | 14.7659 | Y |  | 5
14 | 0.02 | NF | NF | NF | 0.02 | 0.02 | 0.03 | 1868 | 0.78 | 150.561 | 117.4376 | 15.2 | 7.52 | 15.8937 | Y |  | 5
15 | 0.023 | NF | NF | 0.023 | 0.025 | 0.022 | 0.034 | 1869 | 0.76 | 150.4805 | 114.3652 | 14.4 | 7.44 | 16.238 | Y |  | 5
16 | NF | NF | 0.023 | 0.022 | 0.024 | 0.024 | 0.027 | 1890 | 0.76 | 148.8085 | 113.0944 | 14.4 | 7.47 | 16.4192 | Y |  | 5
17 | 0.024 | NF | NF | 0.022 | 0.023 | 0.023 | 0.034 | 1935 | 0.78 | 145.3478 | 113.3713 | 14.2 | 7.53 | 17.0514 | Y |  | 5
18 | NF | NF | NF | 0.021 | 0.023 | 0.023 | 0.034 | 1869 | 0.78 | 150.4805 | 117.3748 | 15.9 | 7.5 | 15.0565 | Y |  | 5
19 | 0.023 | NF | NF | NF | 0.024 | 0.023 | 0.034 | 1896 | 0.81 | 148.3376 | 120.1534 | 14.4 | 7.5 | 16.6971 | Y |  | 5
20 | 0.02 | 0.02 | NF | NF | 0.02 | 0.02 | 0.03 | 1894 | 0.79 | 148.4942 | 117.3104 | 13.7 | 7.65 | 18.4476 | Y |  | 5
21 | 0.02 | 0.02 | NF | 0.02 | 0.03 | NF | 0.03 | 1843 | 0.76 | 152.6034 | 115.9786 | 14 | 7.75 | 18.6995 | Y |  | 5
22 | NF | NF | NF | 0.03 | 0.026 | 0.022 | 0.024 | 1862 | 0.73 | 151.0462 | 110.2637 | 16.1 | 7.64 | 15.5592 | Y |  | 5
23 | 0.023 | 0.027 | 0.024 | NF | 0.028 | 0.025 | 0.028 | 1879 | 0.78 | 149.6796 | 116.7501 | 14.5 | 7.6 | 17.1524 | Y |  | 5
24 | 0.025 | NF | NF | NF | 0.027 | NF | 0.032 | 1877 | 0.74 | 149.8391 | 110.8809 | 14.9 | 7.68 | 17.1251 | Y |  | 5
25 | NF | NF | NF | 0.05 | 0.02 | NF | 0.05 | 1878 | 0.76 | 149.7593 | 113.8171 | 15.2 | 7.64 | 16.5777 | Y |  | 5
26 | 0.027 | 0.026 | 0.026 | 0.022 | 0.023 | NF | 0.046 | 1909 | 0.85 | 147.3274 | 125.2283 | 13.7 | 7.49 | 17.5083 | Y |  | 5
27 | NF | NF | 0.03 | 0.02 | 0.02 | 0.02 | 0.03 | 1907 | 0.78 | 147.4819 | 115.0359 | 14.2 | 7.44 | 16.4933 | Y |  | 5
28 | 0.02 | NF | NF | 0.02 | NF | NF | 0.03 | 1898 | 0.8 | 148.1812 | 118.545 | 14.5 | 7.52 | 16.6905 | Y |  | 5
29 | NF | NF | NF | 0.023 | 0.022 | 0.021 | 0.027 | 1896 | 0.79 | 148.3376 | 117.1867 | 13.1 | 7.49 | 18.0972 | Y |  | 5
30 | 0.021 | 0.021 | 0.022 | NF | 0.022 | 0.023 | 0.032 | 1893 | 0.8 | 148.5726 | 118.8581 | 13.5 | 7.44 | 17.3194 | Y |  | 5
5
AVG. | 0.024556 | 0.025923 | 0.036538 | 0.024762 | 0.028038 | 0.029545 | 0.043034 | 1891.7931 | 0.77862 | 148.6845 | 115.7534 | 14.7728 | 7.5407 | 16.5064
MAX. | 0.05 | 0.05 | 0.18 | 0.05 | 0.14 | 0.17 | 0.18 | 1939
MIN | Conventional Filtration | [7 empty] | 0.7
95% of 4 hr turbidity readings </= 0.3 NTU? Y | [5 empty] | All turbidity readings < IFE2 triggers? Y |  |  |  |  | CT's met everyday? Yes |  |  | All Cl2 Residual at entry point
All the 4 hr turbidity readings </= 1.0 NTU? Y | [13 empty] | >/= 0.2 mg/L Yes
1 Including continuous turbidity data, if applicable, for optimization recording purposes. Compliance values in Columns "12am through 8pm" may not correspond to continuous readings maximum.
2 IFE = Individual Filter Effluent | [7 empty] | Name (Printed): | Jaegar Howatt |  |  | Signature:
3 If Cl2 at entry point <0.2 mg/l, or CT not met, notify DWP by end of next business day. | [7 empty] | Operator Cert. #: | T-448091 |  |  | Date: | 2024-10-05
4 NF=No Flow | [7 empty] | Phone #: | 541-570-7561