## Sheet1
OHA - Drinking Water Program - Turbidity Monitoring Report Form County: Linn Conventional Filtration
Sweet Home, City of |  |  |  | I.D. # OR4100851 |  |  | WTP: WTP-B |  | Month of | 2024-10-01 |  |  |  | Required Log inactivation: |  | 0.5
| TURBIDITY | [5 empty] | Highest | Peak Hourly | Min.Cl2 Res. | CONTACT | ACTUAL | TEMP |  | REQ. | CT | log *
| 12AM | 4AM | 8AM | NOON | 4PM | 8PM | Reading of Day 1 | Demand Flow | at 1st user | TIME | (CT) |  | pH | CT | MET? | inacti-
DATE | NTU | NTU | NTU | NTU | NTU | NTU | (NTU) | (gpm) | Mg/L (C)3 | MIN. (T) | C X T | Co |  | Formula | Y / N | vation
1 | NF | NF | NF | 0.046 | 0.028 | 0.022 | 0.047 | 1924 | 0.8 | 146.1788 | 116.943 | 14.7 | 7.29 | 15.1249 | Y |  | 5
2 | 0.028 | NF | NF | NF | 0.027 | 0.027 | 0.037 | 1689 | 0.8 | 166.5175 | 133.214 | 13.6 | 7.41 | 17.0148 | Y |  | 5
3 | 0.028 | 0.029 | 0.021 | NF | 0.026 | 0.026 | 0.035 | 1685 | 0.77 | 166.9128 | 128.5228 | 14.7 | 7.5 | 16.2925 | Y |  | 5
4 | NF | NF | NF | 0.03 | 0.03 | NF | 0.04 | 1688 | 0.79 | 166.6161 | 131.6267 | 13.4 | 7.41 | 17.2232 | Y |  | 5
5 | NF | NF | NF | 0.03 | 0.03 | 0.03 | 0.031 | 1702 | 0.75 | 165.2456 | 123.9342 | 14.4 | 7.47 | 16.4006 | Y |  | 5
6 | 0.027 | 0.028 | NF | 0.028 | NF | NF | 0.031 | 1705 | 0.78 | 164.9548 | 128.6648 | 13.5 | 7.45 | 17.344 | Y |  | 5
7 | NF | NF | 0.027 | 0.029 | 0.029 | 0.029 | 0.042 | 1743 | 0.67 | 161.3586 | 108.1102 | 15.1 | 7.85 | 17.8516 | Y |  | 5
8 | NF | NF | NF | 0.028 | 0.03 | 0.028 | 0.033 | 1712 | 0.8 | 164.2804 | 131.4243 | 14 | 7.52 | 17.2553 | Y |  | 5
9 | 0.027 | 0.031 | 0.022 | NF | 0.033 | 0.026 | 0.043 | 1684 | 0.84 | 167.0119 | 140.29 | 14.4 | 7.45 | 16.4472 | Y |  | 5
10 | 0.025 | 0.024 | 0.023 | 0.05 | 0.058 | NF | 0.059 | 1684 | 0.79 | 167.0119 | 131.9394 | 15.5 | 7.66 | 16.4263 | Y |  | 5
11 | NF | NF | NF | NF | 0.04 | 0.03 | 0.06 | 1705 | 0.75 | 164.9548 | 123.7161 | 14.8 | 7.5 | 16.1475 | Y |  | 5
12 | 0.03 | 0.03 | 0.04 | NF | NF | 0.04 | 0.04 | 1676 | 0.76 | 167.8091 | 127.5349 | 14.5 | 7.35 | 15.6014 | Y |  | 5
13 | 0.04 | NF | NF | 0.022 | NF | 0.04 | 0.053 | 1696 | 0.74 | 165.8302 | 122.7143 | 15.2 | 7.67 | 16.7245 | Y |  | 5
14 | 0.042 | 0.043 | 0.043 | NF | 0.039 | NF | 0.104 | 1690 | 0.71 | 166.4189 | 118.1574 | 16.3 | 7.61 | 15.1487 | Y |  | 5
15 | NF | NF | NF | 0.033 | 0.035 | 0.035 | 0.061 | 1678 | 0.71 | 167.6091 | 119.0024 | 16.5 | 7.56 | 14.673 | Y |  | 5
16 | 0.034 | NF | NF | 0.032 | 0.032 | 0.022 | 0.035 | 1686 | 0.76 | 166.8138 | 126.7785 | 16.4 | 7.59 | 15.0221 | Y |  | 5
17 | 0.029 | 0.032 | NF | NF | 0.032 | 0.031 | 0.036 | 1657 | 0.79 | 169.7333 | 134.0893 | 17.1 | 7.53 | 14.0679 | Y |  | 5
18 | NF | NF | NF | NF | 0.03 | 0.03 | 0.04 | 1670 | 0.73 | 168.412 | 122.9407 | 16.3 | 7.57 | 14.9597 | Y |  | 5
19 | 0.03 | 0.03 | NF | 0.03 | NF | NF | 0.04 | 1651 | 0.73 | 170.3501 | 124.3556 | 17.8 | 7.63 | 13.8373 | Y |  | 5
20 | 0.022 | 0.024 | NF | NF | 0.029 | 0.027 | 0.032 | 1646 | 0.75 | 170.8676 | 128.1507 | 17.3 | 7.75 | 14.9936 | Y |  | 5
21 | NF | NF | NF | 0.026 | 0.032 | NF | 0.035 | 1647 | 0.74 | 170.7638 | 126.3652 | 17.6 | 7.79 | 14.8988 | Y |  | 5
22 | NF | NF | NF | 0.031 | 0.037 | 0.028 | 0.075 | 1525 | 0.72 | 184.4249 | 132.7859 | 17.6 | 7.85 | 15.1993 | Y |  | 5
23 | 0.031 | NF | NF | 0.029 | 0.028 | 0.029 | 0.043 | 1664 | 0.74 | 169.0192 | 125.0742 | 17.8 | 7.83 | 14.9209 | Y |  | 5
24 | 0.028 | NF | NF | 0.028 | 0.026 | NF | 0.034 | 1680 | 0.72 | 167.4095 | 120.5349 | 17.5 | 7.99 | 16.1154 | Y |  | 5
25 | NF | NF | NF | 0.03 | 0.03 | 0.03 | 0.03 | 1701 | 0.71 | 165.3427 | 117.3933 | 17.9 | 7.79 | 14.5533 | Y |  | 5
26 | 0.03 | 0.03 | 0.03 | NF | NF | NF | 0.03 | 1642 | 0.74 | 171.2838 | 126.75 | 17.9 | 7.87 | 15.0431 | Y |  | 5
27 | NF | NF | 0.028 | 0.03 | 0.026 | 0.032 | 0.035 | 1905 | 0.71 | 147.6367 | 104.8221 | 17.7 | 7.78 | 14.6945 | Y |  | 5
28 | 0.031 | NF | NF | 0.031 | 0.029 | 0.031 | 0.037 | 1865 | 0.57 | 150.8032 | 85.9578 | 18 | 7.88 | 14.7105 | Y |  | 5
29 | 0.028 | NF | NF | 0.031 | 0.03 | 0.028 | 0.059 | 1700 | 0.62 | 165.44 | 102.5728 | 17.5 | 7.81 | 14.9049 | Y |  | 5
30 | NF | NF | NF | 0.035 | 0.034 | NF | 0.041 | 1668 | 0.71 | 168.6139 | 119.7159 | 16.9 | 7.81 | 15.6738 | Y |  | 5
31 | NF | NF | 0.03 | 0.03 | 0.03 | 0.03 | 0.043 | 1680 | 0.67 | 167.4095 | 112.1644 | 16.4 | 7.76 | 15.8356 | Y |  | 5
AVG. | 0.03 | 0.0301 | 0.029333 | 0.031381 | 0.031923 | 0.029591 | 0.043903 | 1698.3226 | 0.73774 | 165.9043 | 122.4595 | 16.0742 | 7.6429 | 15.6486
MAX. | 0.042 | 0.043 | 0.043 | 0.05 | 0.058 | 0.04 | 0.104 | 1924
MIN | Conventional Filtration | [7 empty] | 0.57
95% of 4 hr turbidity readings </= 0.3 NTU? Y | [5 empty] | All turbidity readings < IFE2 triggers? Y |  |  |  |  | CT's met everyday? Yes |  |  | All Cl2 Residual at entry point
All the 4 hr turbidity readings </= 1.0 NTU? Y | [13 empty] | >/= 0.2 mg/L Yes
1 Including continuous turbidity data, if applicable, for optimization recording purposes. Compliance values in Columns "12am through 8pm" may not correspond to continuous readings maximum.
2 IFE = Individual Filter Effluent | [7 empty] | Name (Printed): | Jaegar Howatt |  |  | Signature:
3 If Cl2 at entry point <0.2 mg/l, or CT not met, notify DWP by end of next business day. | [7 empty] | Operator Cert. #: | T-448091 |  |  | Date: | 2024-11-03
4 NF=No Flow | [7 empty] | Phone #: | 541-570-7561