## Sheet1
OHA - Drinking Water Program - Turbidity Monitoring Report Form County: Linn Conventional Filtration
Sweet Home, City of |  |  |  | I.D. # OR4100851 |  |  | WTP: WTP-B |  | Month of | 2024-12-01 |  |  |  | Required Log inactivation: |  | 0.5
| TURBIDITY | [5 empty] | Highest | Peak Hourly | Min.Cl2 Res. | CONTACT | ACTUAL | TEMP |  | REQ. | CT | log *
| 12AM | 4AM | 8AM | NOON | 4PM | 8PM | Reading of Day 1 | Demand Flow | at 1st user | TIME | (CT) |  | pH | CT | MET? | inacti-
DATE | NTU | NTU | NTU | NTU | NTU | NTU | (NTU) | (gpm) | Mg/L (C)3 | MIN. (T) | C X T | Co |  | Formula | Y / N | vation
1 | 0.032 | 0.023 | 0.022 | 0.023 | 0.023 | 0.022 | 0.032 | 1664 | 0.77 | 169.0192 | 130.1448 | 9.6 | 7.73 | 24.947 | Y |  | 5
2 | 0.023 | 0.022 | 0.021 | 0.022 | 0.021 | 0.022 | 0.025 | 1689 | 0.77 | 166.5175 | 128.2184 | 10 | 7.84 | 25.2594 | Y |  | 5
3 | 0.022 | 0.02 | 0.021 | NF | 0.023 | 0.022 | 0.078 | 1687 | 0.77 | 166.7149 | 128.3705 | 10 | 7.71 | 24.1182 | Y |  | 5
4 | 0.021 | 0.021 | 0.023 | NF | NF | 0.022 | 0.025 | 1707 | 0.78 | 164.7616 | 128.514 | 9.7 | 7.43 | 22.31 | Y |  | 5
5 | 0.022 | 0.021 | 0.021 | NF | 0.021 | 0.022 | 0.088 | 1707 | 0.69 | 164.7616 | 113.6855 | 10.1 | 7.53 | 22.2788 | Y |  | 5
6 | 0.02 | NF | NF | NF | 0.02 | 0.06 | 0.07 | 1705 | 0.51 | 164.9548 | 84.127 | 9.5 | 7.45 | 22.0818 | Y |  | 5
7 | NF | NF | NF | 0.02 | 0.02 | 0.02 | 0.03 | 1700 | 0.43 | 165.44 | 71.1392 | 10.9 | 7.54 | 20.5988 | Y |  | 5
8 | 0.02 | 0.043 | 0.028 | 0.021 | NF | NF | 0.061 | 1726 | 0.74 | 162.9479 | 120.5814 | 10.7 | 7.73 | 23.1067 | Y |  | 5
9 | NF | 0.021 | 0.023 | NF | 0.02 | 0.023 | 0.071 | 1710 | 0.68 | 164.4725 | 111.8413 | 9.4 | 7.66 | 24.4083 | Y |  | 5
10 | 0.022 | 0.023 | NF | NF | NF | NF | 0.051 | 1673 | 0.77 | 168.11 | 129.4447 | 13 | 7.46 | 17.9763 | Y |  | 5
11 | NF | NF | NF | NF | 0.029 | 0.022 | 0.029 | 1722 | 0.57 | 163.3264 | 93.096 | 9.4 | 7.59 | 23.5134 | Y |  | 5
12 | 0.021 | 0.021 | 0.02 | 0.02 | 0.029 | 0.02 | 0.029 | 1717 | 0.78 | 163.802 | 127.7655 | 9.5 | 7.65 | 24.4376 | Y |  | 5
13 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | NF | 0.06 | 1691 | 0.78 | 166.3205 | 129.73 | 9.6 | 7.78 | 25.4245 | Y |  | 5
14 | NF | NF | NF | NF | 0.02 | 0.02 | 0.07 | 1704 | 0.71 | 165.0516 | 117.1867 | 9.3 | 7.86 | 26.4794 | Y |  | 5
15 | 0.02 | 0.023 | 0.021 | 0.023 | 0.022 | 0.02 | 0.024 | 1705 | 0.84 | 164.9548 | 138.5621 | 11.7 | 7.45 | 19.8359 | Y |  | 5
16 | 0.021 | 0.02 | 0.02 | NF | 0.022 | 0.021 | 0.037 | 1684 | 0.77 | 167.0119 | 128.5991 | 10 | 7.89 | 25.7138 | Y |  | 5
17 | NF | NF | NF | NF | NF | NF | NF | NF | NF | #VALUE! | #VALUE! | NF | NF | #VALUE! |  |  | 5
18 | NF | NF | NF | NF | 0.028 | 0.046 | 0.08 | 1737 | 0.65 | 161.9159 | 105.2454 | 10.5 | 7.74 | 23.2592 | Y |  | 5
19 | 0.05 | 0.06 | 0.09 | 0.05 | 0.06 | 0.06 | 0.1 | 1727 | 0.87 | 162.8535 | 141.6825 | 10.3 | 7.99 | 26.4203 | Y |  | 5
20 | 0.02 | 0.03 | NF | 0.02 | 0.02 | NF | 0.03 | 1687 | 0.85 | 166.7149 | 141.7076 | 10.4 | 7.6 | 22.7959 | Y |  | 5
21 | NF | NF | NF | 0.02 | 0.02 | 0.02 | 0.03 | 1708 | 0.81 | 164.6651 | 133.3787 | 11 | 7.7 | 22.5922 | Y |  | 5
22 | 0.021 | NF | NF | NF | 0.021 | 0.02 | 0.024 | 1690 | 0.85 | 166.4189 | 141.4561 | 11.3 | 7.48 | 20.5981 | Y |  | 5
23 | 0.02 | 0.022 | NF | 0.023 | 0.02 | NF | 0.038 | 1674 | 0.81 | 168.0096 | 136.0877 | 10.6 | 7.61 | 22.4736 | Y |  | 5
24 | NF | NF | NF | NF | NF | NF | NF | NF | NF | #VALUE! | #VALUE! | NF | NF | #VALUE! |  |  | 5
25 | NF | NF | NF | 0.022 | NF | NF | 0.028 | 1699 | 0.68 | 165.5374 | 112.5654 | 10.6 | 7.67 | 22.6185 | Y |  | 5
26 | NF | NF | NF | 0.021 | 0.021 | 0.025 | 0.037 | 1707 | 0.82 | 164.7616 | 135.1045 | 11.1 | 7.57 | 21.4653 | Y |  | 5
27 | 0.02 | 0.06 | 0.07 | 0.07 | 0.023 | 0.02 | 0.07 | 1685 | 0.86 | 166.9128 | 143.545 | 11.6 | 7.69 | 21.7612 | Y |  | 5
28 | 0.02 | NF | NF | NF | 0.02 | 0.02 | 0.04 | 1701 | 0.8 | 165.3427 | 132.2742 | 14.5 | 7.62 | 17.319 | Y |  | 5
29 | 0.02 | 0.02 | NF | NF | NF | 0.023 | 0.032 | 1687 | 0.82 | 166.7149 | 136.7062 | 10.3 | 7.63 | 23.113 | Y |  | 5
30 | 0.022 | 0.021 | 0.022 | NF | 0.021 | NF | 0.032 | 1707 | 0.83 | 164.7616 | 136.7521 | 11.7 | 7.57 | 20.6593 | Y |  | 5
31 | 0.022 | NF | NF | 0.021 | 0.022 | NF | 0.028 | 1685 | 0.84 | 166.9128 | 140.2067 | 13.6 | 7.57 | 18.1329 | Y |  | 5
AVG. | 0.02281 | 0.027278 | 0.030143 | 0.0264 | 0.023583 | 0.02619 | 0.046517 | 1699.4828 | 0.75345 | #VALUE! | #VALUE! | 10.6862 | 7.6462 | #VALUE!
MAX. | 0.05 | 0.06 | 0.09 | 0.07 | 0.06 | 0.06 | 0.1 | 1737
MIN | Conventional Filtration | [7 empty] | 0.43
95% of 4 hr turbidity readings </= 0.3 NTU? Y | [5 empty] | All turbidity readings < IFE2 triggers? Y |  |  |  |  | CT's met everyday? Yes |  |  | All Cl2 Residual at entry point
All the 4 hr turbidity readings </= 1.0 NTU? Y | [13 empty] | >/= 0.2 mg/L Yes
1 Including continuous turbidity data, if applicable, for optimization recording purposes. Compliance values in Columns "12am through 8pm" may not correspond to continuous readings maximum.
2 IFE = Individual Filter Effluent | [7 empty] | Name (Printed): | Jaegar T Howatt |  |  | Signature:
3 If Cl2 at entry point <0.2 mg/l, or CT not met, notify DWP by end of next business day. | [7 empty] | Operator Cert. #: | T-448091 |  |  | Date: | 2024-01-06
4 NF=No Flow | [7 empty] | Phone #: | 541-570-7561