## Sheet1
OHA - Drinking Water Program - Turbidity Monitoring Report Form County: Linn Conventional Filtration
Sweet Home, City of |  |  |  | I.D. # OR4100851 |  |  | WTP: WTP-B |  | Month of | 2025-01-01 |  |  |  | Required Log inactivation: |  | 0.5
| TURBIDITY | [5 empty] | Highest | Peak Hourly | Min.Cl2 Res. | CONTACT | ACTUAL | TEMP |  | REQ. | CT | log *
| 12AM | 4AM | 8AM | NOON | 4PM | 8PM | Reading of Day 1 | Demand Flow | at 1st user | TIME | (CT) |  | pH | CT | MET? | inacti-
DATE | NTU | NTU | NTU | NTU | NTU | NTU | (NTU) | (gpm) | Mg/L (C)3 | MIN. (T) | C X T | Co |  | Formula | Y / N | vation
1 | NF | NF | NF | NF | NF | NF | NF | NF | NF | #VALUE! | #VALUE! | NF | NF | #VALUE! | #VALUE! |  | 5
2 | NF | NF | NF | NF | 0.022 | 0.02 | 0.074 | 1707 | 0.62 | 164.7616 | 102.1522 | 11.2 | 7.6 | 21.0702 | Y |  | 5
3 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03 | 1694 | 0.87 | 166.026 | 144.4426 | 10.2 | 7.78 | 24.6781 | Y |  | 5
4 | 0.02 | NF | NF | NF | 0.02 | 0.02 | 0.06 | 1703 | 0.81 | 165.1486 | 133.7703 | 13 | 7.79 | 20.3944 | Y |  | 5
5 | 0.02 | 0.02 | NF | NF | 0.02 | NF | 0.03 | 1662 | 0.77 | 169.2226 | 130.3014 | 10 | 7.77 | 24.6377 | Y |  | 5
6 | NF | NF | NF | NF | NF | NF | NF | NF | NF | #VALUE! | #VALUE! | NF | NF | #VALUE! | #VALUE! |  | 5
7 | NF | 0.022 | 0.023 | 0.02 | 0.021 | 0.021 | 0.024 | 1689 | 0.68 | 166.5175 | 113.2319 | 10.9 | 7.67 | 22.1744 | Y |  | 5
8 | 0.021 | NF | NF | 0.02 | 0.02 | 0.021 | 0.028 | 1689 | 0.82 | 166.5175 | 136.5443 | 10.6 | 7.78 | 23.8924 | Y |  | 5
9 | 0.021 | NF | NF | NF | 0.02 | 0.021 | 0.023 | 1677 | 0.8 | 167.709 | 134.1672 | 10.6 | 7.77 | 23.7537 | Y |  | 5
10 | 0.02 | NF | NF | 0.02 | 0.02 | 0.02 | 0.03 | 1685 | 0.81 | 166.9128 | 135.1993 | 10.6 | 7.74 | 23.5294 | Y |  | 5
11 | 0.04 | NF | NF | 0.05 | NF | 0.05 | 0.05 | 1704 | 0.8 | 165.0516 | 132.0413 | 13.4 | 7.8 | 19.9113 | Y |  | 5
12 | 0.04 | NF | NF | 0.05 | NF | 0.05 | 0.05 | 1704 | 0.8 | 165.0516 | 132.0413 | 11.6 | 7.77 | 22.2306 | Y |  | 5
13 | NF | NF | NF | NF | NF | NF | NF | NF | NF | #VALUE! | #VALUE! | NF | NF | #VALUE! | #VALUE! |  | 5
14 | NF | NF | NF | NF | NF | 0.021 | 0.024 | 1722 | 0.69 | 163.3264 | 112.6952 | 10.9 | 7.84 | 23.5723 | Y |  | 5
15 | 0.021 | 0.021 | 0.019 | 0.022 | 0.021 | 0.021 | 0.025 | 1697 | 0.81 | 165.7325 | 134.2433 | 12.4 | 7.81 | 21.4114 | Y |  | 5
16 | 0.021 | NF | NF | 0.021 | 0.021 | NF | 0.022 | 1678 | 0.79 | 167.6091 | 132.4112 | 10.4 | 7.79 | 24.2157 | Y |  | 5
17 | NF | NF | NF | 0.02 | 0.02 | 0.03 | 0.03 | 1696 | 0.76 | 165.8302 | 126.0309 | 10.7 | 7.72 | 23.0776 | Y |  | 5
18 | 0.02 | 0.02 | NF | NF | NF | 0.02 | 0.02 | 1663 | 0.75 | 169.1209 | 126.8406 | 12 | 7.7 | 21.0087 | Y |  | 5
19 | 0.023 | NF | NF | NF | 0.021 | 0.021 | 0.023 | 1698 | 0.72 | 165.6349 | 119.2571 | 9.4 | 7.74 | 25.2281 | Y |  | 5
20 | NF | NF | NF | NF | NF | NF | NF | NF | NF | #VALUE! | #VALUE! | NF | NF | #VALUE! | #VALUE! |  | 5
21 | NF | NF | NF | NF | NF | NF | 0.032 | 1681 | 0.67 | 167.3099 | 112.0977 | 11.6 | 7.89 | 22.852 | Y |  | 5
22 | NF | NF | NF | 0.023 | 0.021 | 0.021 | 0.025 | 1715 | 0.69 | 163.993 | 113.1552 | 10.3 | 7.67 | 23.0986 | Y |  | 5
23 | 0.021 | 0.021 | 0.025 | 0.022 | 0.021 | 0.021 | 0.027 | 1699 | 0.74 | 165.5374 | 122.4977 | 10.3 | 7.7 | 23.4779 | Y |  | 5
24 | 0.02 | NF | NF | 0.02 | NF | 0.02 | 0.03 | 1882 | 0.71 | 149.441 | 106.1031 | 9.1 | 7.73 | 25.6187 | Y |  | 5
25 | 0.02 | 0.02 | 0.02 | NF | NF | NF | 0.03 | 1862 | 0.73 | 151.0462 | 110.2637 | 12.1 | 7.67 | 20.6075 | Y |  | 5
26 | NF | NF | NF | 0.02 | 0.02 | 0.02 | 0.02 | 1868 | 0.69 | 150.561 | 103.8871 | 10.6 | 7.72 | 23.0472 | Y |  | 5
27 | 0.022 | 0.022 | 0.022 | NF | 0.018 | NF | 0.026 | 1862 | 0.7 | 151.0462 | 105.7323 | 12 | 7.7 | 20.891 | Y |  | 5
28 | NF | NF | NF | 0.02 | NF | NF | 0.03 | 1865 | 0.65 | 150.8032 | 98.0221 | 9.5 | 7.66 | 24.1634 | Y |  | 5
29 | NF | NF | NF | 0.021 | 0.021 | 0.022 | 0.032 | 1877 | 0.68 | 149.8391 | 101.8906 | 9.1 | 7.72 | 25.4399 | Y |  | 5
30 | 0.023 | 0.022 | 0.017 | NF | NF | NF | 0.026 | 1817 | 0.7 | 154.787 | 108.3509 | 11.1 | 7.77 | 22.7192 | Y |  | 5
31 | NF | NF | NF | 0.021 | 0.05 | NF | 0.06 | 1838 | 0.64 | 153.0185 | 97.9318 | 9.1 | 7.66 | 24.7882 | Y |  | 5
AVG. | 0.023118 | 0.020889 | 0.020857 | 0.024375 | 0.022056 | 0.024211 | 0.03263 | 1742 | 0.73704 | #VALUE! | #VALUE! | 10.8407 | 7.7393 | #VALUE!
MAX. | 0.04 | 0.022 | 0.025 | 0.05 | 0.05 | 0.05 | 0.074 | 1882
MIN | Conventional Filtration | [7 empty] | 0.62
95% of 4 hr turbidity readings </= 0.3 NTU? Y | [5 empty] | All turbidity readings < IFE2 triggers? Y |  |  |  |  | CT's met everyday? Yes |  |  | All Cl2 Residual at entry point
All the 4 hr turbidity readings </= 1.0 NTU? Y | [13 empty] | >/= 0.2 mg/L Yes
1 Including continuous turbidity data, if applicable, for optimization recording purposes. Compliance values in Columns "12am through 8pm" may not correspond to continuous readings maximum.
2 IFE = Individual Filter Effluent | [7 empty] | Name (Printed): | Jaegar T Howatt |  |  | Signature:
3 If Cl2 at entry point <0.2 mg/l, or CT not met, notify DWP by end of next business day. | [7 empty] | Operator Cert. #: | T-448091 |  |  | Date: | 2025-02-04
4 NF=No Flow | [7 empty] | Phone #: | 541-570-7561