## Sheet1
OHA - Drinking Water Program - Turbidity Monitoring Report Form County: Linn Conventional Filtration
Sweet Home, City of |  |  |  | I.D. # OR4100851 |  |  | WTP: WTP-B |  | Month of | 2025-02-25 |  |  |  | Required Log inactivation: |  | 0.5
| TURBIDITY | [5 empty] | Highest | Peak Hourly | Min.Cl2 Res. | CONTACT | ACTUAL | TEMP |  | REQ. | CT | log *
| 12AM | 4AM | 8AM | NOON | 4PM | 8PM | Reading of Day 1 | Demand Flow | at 1st user | TIME | (CT) |  | pH | CT | MET? | inacti-
DATE | NTU | NTU | NTU | NTU | NTU | NTU | (NTU) | (gpm) | Mg/L (C)3 | MIN. (T) | C X T | Co |  | Formula | Y / N | vation
1 | NF | NF | NF | 0.02 | 0.02 | 0.03 | 0.02 | 1852 | 0.67 | 151.8618 | 101.7474 | 9.7 | 7.7 | 24.2398 | Y |  | 5
2 | 0.02 | NF | NF | 0.02 | 0.02 | 0.02 | 0.03 | 1844 | 0.74 | 152.5206 | 112.8652 | 11.1 | 7.77 | 22.8224 | Y |  | 5
3 | 0.02 | NF | NF | NF | NF | 0.02 | 0.02 | 1837 | 0.71 | 153.1018 | 108.7023 | 7.9 | 7.71 | 27.5713 | Y |  | 5
4 | NF | NF | NF | 0.022 | 0.023 | 0.021 | 0.023 | 1948 | 0.74 | 144.3778 | 106.8396 | 12.4 | 7.69 | 20.3711 | Y |  | 5
5 | NF | NF | NF | 0.021 | 0.018 | NF | 0.028 | 1936 | 0.74 | 145.2727 | 107.5018 | 9.1 | 7.55 | 24.1119 | Y |  | 5
6 | NF | NF | NF | 0.025 | 0.023 | 0.023 | 0.025 | 1944 | 0.69 | 144.6749 | 99.8257 | 9.1 | 7.63 | 24.6657 | Y |  | 5
7 | NF | NF | NF | NF | 0.018 | 0.022 | 0.032 | 1948 | 0.69 | 144.3778 | 99.6207 | 9.6 | 7.66 | 24.1127 | Y |  | 5
8 | 0.02 | NF | NF | 0.02 | 0.02 | NF | 0.03 | 1937 | 0.71 | 145.1977 | 103.0904 | 10.2 | 7.64 | 23.0594 | Y |  | 5
9 | NF | NF | NF | 0.02 | 0.02 | 0.02 | 0.03 | 1931 | 0.67 | 145.6489 | 97.5848 | 9.7 | 7.64 | 23.7295 | Y |  | 5
10 | 0.021 | NF | NF | 0.022 | 0.023 | 0.022 | 0.037 | 1932 | 0.73 | 145.5735 | 106.2687 | 9.7 | 7.65 | 23.977 | Y |  | 5
11 | NF | NF | NF | 0.02 | 0.03 | NF | 0.03 | 1958 | 0.72 | 143.6404 | 103.4211 | 9.6 | 7.62 | 23.8545 | Y |  | 5
12 | NF | NF | NF | 0.021 | 0.027 | 0.022 | 0.031 | 1944 | 0.71 | 144.6749 | 102.7192 | 9.2 | 7.57 | 24.0401 | Y |  | 5
13 | NF | NF | NF | 0.022 | 0.021 | 0.021 | 0.026 | 1952 | 0.7 | 144.082 | 100.8574 | 10.5 | 7.62 | 22.4216 | Y |  | 5
14 | NF | NF | NF | 0.021 | 0.021 | 0.023 | 0.098 | 1944 | 0.71 | 144.6749 | 102.7192 | 8.8 | 7.6 | 24.9545 | Y |  | 5
15 | NF | NF | NF | 0.02 | 0.02 | 0.02 | 0.02 | 1944 | 0.72 | 144.6749 | 104.1659 | 8.9 | 7.67 | 25.4434 | Y |  | 5
16 | NF | NF | NF | 0.02 | 0.02 | NF | 0.03 | 1953 | 0.71 | 144.0082 | 102.2458 | 9.3 | 7.62 | 24.308 | Y |  | 5
17 | NF | NF | NF | 0.02 | 0.02 | NF | 0.03 | 1982 | 0.71 | 141.9011 | 100.7498 | 8.8 | 7.71 | 25.9529 | Y |  | 5
18 | 0.02 | NF | NF | NF | 0.02 | 0.02 | 0.03 | 1942 | 0.69 | 144.8239 | 99.9285 | 9 | 7.68 | 25.277 | Y |  | 5
19 | 0.018 | NF | NF | 0.032 | NF | NF | 0.032 | 1946 | 0.71 | 144.5262 | 102.6136 | 9.1 | 7.76 | 25.8946 | Y |  | 5
20 | NF | NF | NF | 0.024 | 0.023 | 0.022 | 0.038 | 1921 | 0.67 | 146.4071 | 98.0927 | 10 | 7.7 | 23.7606 | Y |  | 5
21 | NF | NF | NF | NF | 0.023 | 0.018 | 0.032 | 1911 | 0.71 | 147.1732 | 104.493 | 9.6 | 7.65 | 24.0822 | Y |  | 5
22 | 0.02 | 0.02 | NF | NF | 0.03 | 0.02 | 0.03 | 1898 | 0.74 | 148.1812 | 109.6541 | 10.1 | 7.62 | 23.1279 | Y |  | 5
23 | NF | NF | NF | 0.02 | 0.02 | 0.02 | 0.02 | 1920 | 0.74 | 146.4833 | 108.3977 | 12.4 | 7.75 | 20.8021 | Y |  | 5
24 | 0.02 | NF | NF | NF | 0.02 | NF | 0.04 | 1905 | 0.77 | 147.6367 | 113.6803 | 12.3 | 7.62 | 20.0781 | Y |  | 5
25 | NF | NF | NF | 0.02 | 0.02 | 0.02 | 0.09 | 1907 | 0.74 | 147.4819 | 109.1366 | 11.1 | 7.52 | 20.9038 | Y |  | 5
26 | NF | NF | NF | 0.022 | 0.022 | 0.022 | 0.066 | 1920 | 0.82 | 146.4833 | 120.1163 | 10 | 7.58 | 23.1645 | Y |  | 5
27 | 0.02 | 0.02 | 0.017 | 0.017 | 0.02 | 0.02 | 0.035 | 1902 | 0.78 | 147.8696 | 115.3383 | 11.6 | 7.74 | 21.9477 | Y |  | 5
28 | 0.02 | NF | NF | NF | 0.02 | 0.022 | 0.046 | 1756 | 0.75 | 160.164 | 120.123 | 11.2 | 7.76 | 22.6176 | Y |  | 5
29 | [9 empty] | #DIV/0! | #DIV/0! |  |  | 4.185 | #DIV/0! |  | 5
30 | [9 empty] | #DIV/0! | #DIV/0! |  |  | 4.185 | #DIV/0! |  | 5
31 | [9 empty] | #DIV/0! | #DIV/0! |  |  | 4.185 | #DIV/0! |  | 5
AVG. | 0.0199 | 0.02 | 0.017 | 0.021381 | 0.021615 | 0.021333 | 0.035679 | 1918.3571 | 0.72107 | #DIV/0! | #DIV/0! | 10 | 7.6582 | 21.737
MAX. | 0.021 | 0.02 | 0.017 | 0.032 | 0.03 | 0.03 | 0.098 | 1982
MIN | Conventional Filtration | [7 empty] | 0.67
95% of 4 hr turbidity readings </= 0.3 NTU? Y | [5 empty] | All turbidity readings < IFE2 triggers? Y |  |  |  |  | CT's met everyday? Yes |  |  | All Cl2 Residual at entry point
All the 4 hr turbidity readings </= 1.0 NTU? Y | [13 empty] | >/= 0.2 mg/L Yes
1 Including continuous turbidity data, if applicable, for optimization recording purposes. Compliance values in Columns "12am through 8pm" may not correspond to continuous readings maximum.
2 IFE = Individual Filter Effluent | [7 empty] | Name (Printed): | Jaegar Howatt |  |  | Signature:
3 If Cl2 at entry point <0.2 mg/l, or CT not met, notify DWP by end of next business day. | [7 empty] | Operator Cert. #: | T-448091 |  |  | Date: | 2025-03-03
4 NF=No Flow | [7 empty] | Phone #: | 541-570-7561