## Sheet1
OHA - Drinking Water Program - Turbidity Monitoring Report Form County: Linn Conventional Filtration
Sweet Home, City of |  |  |  | I.D. # OR4100851 |  |  | WTP: WTP-B |  | Month of | 2025-03-01 |  |  |  | Required Log inactivation: |  | 0.5
| TURBIDITY | [5 empty] | Highest | Peak Hourly | Min.Cl2 Res. | CONTACT | ACTUAL | TEMP |  | REQ. | CT | log *
| 12AM | 4AM | 8AM | NOON | 4PM | 8PM | Reading of Day 1 | Demand Flow | at 1st user | TIME | (CT) |  | pH | CT | MET? | inacti-
DATE | NTU | NTU | NTU | NTU | NTU | NTU | (NTU) | (gpm) | Mg/L (C)3 | MIN. (T) | C X T | Co |  | Formula | Y / N | vation
1 | 0.05 | NF | NF | 0.02 | 0.02 | 0.02 | 0.05 | 1723 | 0.74 | 163.2316 | 120.7914 | 11 | 7.74 | 22.7321 | Y |  | 5
2 | 0.02 | 0.02 | NF | NF | 0.02 | 0.03 | 0.03 | 1723 | 0.76 | 163.2316 | 124.056 | 11.3 | 7.79 | 22.7332 | Y |  | 5
3 | 0.02 | NF | 0.02 | NF | NF | 0.02 | 0.02 | 1722 | 0.69 | 163.3264 | 112.6952 | 10.8 | 7.86 | 23.8983 | Y |  | 5
4 | NF | NF | NF | 0.02 | 0.02 | 0.02 | 0.02 | 1721 | 0.76 | 163.4213 | 124.2002 | 14 | 7.82 | 19.1885 | Y |  | 5
5 | 0.022 | 0.021 | NF | NF | 0.02 | 0.021 | 0.023 | 1696 | 0.75 | 165.8302 | 124.3726 | 12 | 7.8 | 21.758 | Y |  | 5
6 | NF | NF | NF | 0.02 | 0.02 | 0.027 | 0.027 | 1730 | 0.73 | 162.5711 | 118.6769 | 12.3 | 7.85 | 21.6611 | Y |  | 5
7 | 0.022 | NF | NF | NF | 0.02 | 0.021 | 0.025 | 1729 | 0.69 | 162.6651 | 112.2389 | 11.6 | 7.82 | 22.3456 | Y |  | 5
8 | 0.02 | NF | NF | NF | 0.02 | 0.03 | 0.03 | 1734 | 0.71 | 162.1961 | 115.1592 | 12.8 | 7.85 | 20.8904 | Y |  | 5
9 | 0.02 | NF | NF | 0.03 | 0.02 | 0.02 | 0.03 | 1755 | 0.67 | 160.2553 | 107.371 | 11.1 | 7.64 | 21.63 | Y |  | 5
10 | 0.02 | NF | NF | 0.02 | 0.02 | 0.03 | 0.04 | 1713 | 0.65 | 164.1845 | 106.7199 | 12.6 | 7.73 | 20.1171 | Y |  | 5
11 | NF | NF | NF | 0.022 | 0.018 | 0.02 | 0.032 | 1703 | 0.65 | 165.1486 | 107.3466 | 10.7 | 7.7 | 22.6312 | Y |  | 5
12 | 0.021 | NF | NF | 0.022 | 0.02 | NF | 0.029 | 1696 | 0.71 | 165.8302 | 117.7394 | 12.9 | 7.88 | 20.9828 | Y |  | 5
13 | NF | 0.023 | 0.022 | NF | 0.022 | 0.018 | 0.026 | 1736 | 0.68 | 162.0092 | 110.1663 | 11.6 | 8.04 | 24.1253 | Y |  | 5
14 | NF | NF | NF | 0.023 | 0.03 | 0.03 | 0.03 | 1712 | 0.7 | 164.2804 | 114.9963 | 12.1 | 7.65 | 20.3956 | Y |  | 5
15 | NF | NF | NF | 0.02 | 0.02 | 0.02 | 0.03 | 1717 | 0.69 | 163.802 | 113.0234 | 11 | 7.75 | 22.6835 | Y |  | 5
16 | NF | NF | 0.02 | 0.02 | 0.02 | NF | 0.03 | 1727 | 0.67 | 162.8535 | 109.1118 | 12.5 | 7.76 | 20.5223 | Y |  | 5
17 | NF | 0.02 | 0.03 | 0.02 | NF | NF | 0.08 | 1742 | 0.68 | 161.4512 | 109.7868 | 11.3 | 7.77 | 22.3699 | Y |  | 5
18 | NF | NF | 0.02 | 0.02 | 0.02 | NF | 0.08 | 1724 | 0.65 | 163.1369 | 106.039 | 12.1 | 7.73 | 20.8558 | Y |  | 5
19 | NF | 0.022 | 0.02 | 0.022 | 0.02 | NF | 0.035 | 1722 | 0.67 | 163.3264 | 109.4287 | 10.3 | 7.83 | 24.3901 | Y |  | 5
20 | NF | 0.02 | 0.019 | 0.02 | 0.02 | NF | 0.026 | 1700 | 0.7 | 165.44 | 115.808 | 11.8 | 7.85 | 22.3116 | Y |  | 5
21 | NF | 0.025 | 0.02 | NF | 0.022 | 0.021 | 0.069 | 1718 | 0.74 | 163.7066 | 121.1429 | 11.1 | 7.69 | 22.188 | Y |  | 5
22 | NF | NF | NF | 0.02 | NF | NF | 0.09 | 1710 | 0.71 | 164.4725 | 116.7755 | 10.4 | 7.83 | 24.3389 | Y |  | 5
23 | NF | NF | NF | 0.02 | 0.02 | 0.02 | 0.04 | 1741 | 0.76 | 161.5439 | 122.7734 | 10.5 | 7.86 | 24.5761 | Y |  | 5
24 | 0.02 | 0.02 | NF | 0.02 | 0.02 | NF | 0.037 | 1772 | 0.8 | 158.7178 | 126.9743 | 10.7 | 7.89 | 24.6227 | Y |  | 5
25 | NF | NF | 0.02 | 0.02 | 0.022 | NF | 0.069 | 1709 | 0.78 | 164.5688 | 128.3636 | 12.9 | 7.9 | 21.3059 | Y |  | 5
26 | NF | 0.024 | 0.02 | 0.021 | NF | NF | 0.027 | 1714 | 0.85 | 164.0887 | 139.4754 | 11.5 | 7.67 | 21.7272 | Y |  | 5
27 | NF | NF | NF | 0.022 | 0.021 | 0.021 | 0.08 | 1713 | 0.83 | 164.1845 | 136.2731 | 11.7 | 7.65 | 21.2454 | Y |  | 5
28 | 0.022 | NF | NF | 0.022 | 0.03 | 0.03 | 0.026 | 1768 | 0.79 | 159.0769 | 125.6708 | 11.8 | 7.65 | 21.0116 | Y |  | 5
29 | 0.02 | NF | NF | 0.02 | 0.02 | 0.02 | 0.04 | 1718 | 0.78 | 163.7066 | 127.6912 | 12.6 | 7.67 | 19.9693 | Y |  | 5
30 | NF | NF | 0.02 | NF | NF | NF | 0.02 | 1747 | 0.77 | 160.9891 | 123.9616 | 11.6 | 7.65 | 21.2416 | Y |  | 5
31 | NF | NF | NF | 0.02 | 0.02 | 0.02 | 0.03 | 1715 | 0.78 | 163.993 | 127.9145 | 11.1 | 7.77 | 22.9262 | Y |  | 5
AVG. | 0.023083 | 0.021667 | 0.021 | 0.021043 | 0.020962 | 0.02295 | 0.039387 | 1724.1935 | 0.7271 | 163.1368 | 118.6046 | 11.6677 | 7.7771 | 22.0444
MAX. | 0.05 | 0.025 | 0.03 | 0.03 | 0.03 | 0.03 | 0.09 | 1772
MIN | Conventional Filtration | [7 empty] | 0.65
95% of 4 hr turbidity readings </= 0.3 NTU? Y | [5 empty] | All turbidity readings < IFE2 triggers? Y |  |  |  |  | CT's met everyday? Yes |  |  | All Cl2 Residual at entry point
All the 4 hr turbidity readings </= 1.0 NTU? Y | [13 empty] | >/= 0.2 mg/L Yes
1 Including continuous turbidity data, if applicable, for optimization recording purposes. Compliance values in Columns "12am through 8pm" may not correspond to continuous readings maximum.
2 IFE = Individual Filter Effluent | [7 empty] | Name (Printed): | Jaegat T Howatt |  |  | Signature:
3 If Cl2 at entry point <0.2 mg/l, or CT not met, notify DWP by end of next business day. | [7 empty] | Operator Cert. #: | T-448091 |  |  | Date: | 2025-04-01
4 NF=No Flow | [7 empty] | Phone #: | 541-570-7561