## Sheet1
OHA - Drinking Water Program - Turbidity Monitoring Report Form County: Linn Conventional Filtration
Sweet Home, City of |  |  |  | I.D. # OR4100851 |  |  | WTP: WTP-B |  | Month of | 2025-04-01 |  |  |  | Required Log inactivation: |  | 0.5
| TURBIDITY | [5 empty] | Highest | Peak Hourly | Min.Cl2 Res. | CONTACT | ACTUAL | TEMP |  | REQ. | CT | log *
| 12AM | 4AM | 8AM | NOON | 4PM | 8PM | Reading of Day 1 | Demand Flow | at 1st user | TIME | (CT) |  | pH | CT | MET? | inacti-
DATE | NTU | NTU | NTU | NTU | NTU | NTU | (NTU) | (gpm) | Mg/L (C)3 | MIN. (T) | C X T | Co |  | Formula | Y / N | vation
1 | NF | NF | 0.021 | 0.021 | 0.018 | NF | 0.055 | 1720 | 0.78 | 163.5163 | 127.5427 | 10.8 | 7.82 | 23.8046 | Y |  | 5
2 | NF | 0.024 | NF | 0.022 | 0.021 | 0.021 | 0.031 | 1736 | 0.78 | 162.0092 | 126.3672 | 11.2 | 7.78 | 22.8554 | Y |  | 5
3 | NF | NF | NF | NF | 0.02 | 0.02 | 0.026 | 1732 | 0.76 | 162.3834 | 123.4114 | 12.2 | 7.81 | 21.5731 | Y |  | 5
4 | 0.023 | 0.022 | 0.022 | NF | 0.02 | 0.02 | 0.023 | 1731 | 0.78 | 162.4772 | 126.7322 | 12.3 | 7.81 | 21.48 | Y |  | 5
5 | NF | NF | 0.02 | 0.02 | 0.02 | NF | 0.02 | 1729 | 0.8 | 162.6651 | 130.1321 | 12.6 | 7.75 | 20.613 | Y |  | 5
6 | 0.02 | NF | 0.02 | 0.02 | 0.02 | 0.02 | 0.03 | 1730 | 0.83 | 162.5711 | 134.934 | 12.9 | 7.7 | 19.9058 | Y |  | 5
7 | 0.02 | 0.02 | 0.02 | NF | NF | NF | 0.04 | 1709 | 0.82 | 164.5688 | 134.9464 | 12.6 | 7.8 | 21.0434 | Y |  | 5
8 | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF |  | 5
9 | NF | NF | 0.02 | 0.02 | 0.02 | 0.02 | 0.1 | 2538 | 0.48 | 110.8148 | 53.1911 | 12 | 7.67 | 20.17 | Y |  | 5
10 | NF | NF | 0.02 | 0.02 | 0.02 | NF | 0.09 | 2561 | 0.61 | 109.8196 | 66.99 | 12.6 | 7.63 | 19.3017 | Y |  | 5
11 | NF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.07 | 1962 | 0.67 | 143.3476 | 96.0429 | 12.6 | 7.65 | 19.5772 | Y |  | 5
12 | 0.02 | NF | NF | 0.02 | 0.02 | 0.02 | 0.04 | 1978 | 0.63 | 142.1881 | 89.5785 | 13.2 | 7.7 | 19.0761 | Y |  | 5
13 | 0.02 | NF | NF | 0.06 | 0.02 | 0.02 | 0.1 | 2476 | 0.66 | 113.5897 | 74.9692 | 12.9 | 7.67 | 19.3113 | Y |  | 5
14 | NF | NF | 0.03 | 0.03 | 0.02 | NF | 0.04 | 2451 | 0.64 | 114.7483 | 73.4389 | 13.2 | 7.72 | 19.2391 | Y |  | 5
15 | NF | NF | NF | 0.02 | 0.02 | NF | 0.05 | 2479 | 0.62 | 113.4522 | 70.3404 | 15.9 | 7.8 | 16.522 | Y |  | 5
16 | NF | NF | NF | 0.029 | 0.031 | 0.03 | 0.069 | 2505 | 0.64 | 112.2747 | 71.8558 | 13.8 | 7.79 | 18.9712 | Y |  | 5
17 | NF | NF | NF | 0.03 | 0.031 | NF | 0.044 | 2474 | 0.68 | 113.6815 | 77.3034 | 14.2 | 7.83 | 18.8337 | Y |  | 5
18 | NF | NF | NF | 0.034 | 0.031 | NF | 0.038 | 2480 | 0.66 | 113.4065 | 74.8483 | 14.5 | 7.78 | 18.0835 | Y |  | 5
19 | NF | NF | NF | 0.02 | 0.02 | NF | 0.07 | 2486 | 0.67 | 113.1327 | 75.7989 | 14.7 | 7.83 | 18.1977 | Y |  | 5
20 | NF | NF | NF | 0.02 | 0.02 | 0.02 | 0.07 | 2492 | 0.66 | 112.8604 | 74.4878 | 14.2 | 7.81 | 18.6529 | Y |  | 5
21 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | NF | 0.06 | 2446 | 0.68 | 114.9828 | 78.1883 | 13.9 | 7.76 | 18.723 | Y |  | 5
22 | NF | NF | NF | 0.02 | 0.03 | NF | 0.09 | 2461 | 0.67 | 114.282 | 76.5689 | 15.9 | 7.82 | 16.7396 | Y |  | 5
23 | NF | NF | NF | 0.03 | NF | NF | 0.04 | 2484 | 0.67 | 113.2238 | 75.86 | 16.1 | 7.73 | 15.977 | Y |  | 5
24 | NF | NF | NF | 0.028 | 0.028 | NF | 0.038 | 2302 | 0.67 | 122.1755 | 81.8576 | 15.4 | 7.68 | 16.433 | Y |  | 5
25 | NF | NF | NF | 0.03 | 0.033 | NF | 0.042 | 2429 | 0.64 | 115.7876 | 74.104 | 14.3 | 7.72 | 17.8834 | Y |  | 5
26 | NF | NF | NF | 0.02 | 0.02 | 0.02 | 0.06 | 2222 | 0.71 | 126.5743 | 89.8677 | 14.4 | 7.71 | 17.8406 | Y |  | 5
27 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | NF | 0.06 | 2429 | 0.71 | 115.7876 | 82.2092 | 14.2 | 7.75 | 18.3483 | Y |  | 5
28 | NF | NF | NF | 0.032 | 0.032 | 0.032 | 0.038 | 2423 | 0.67 | 116.0743 | 77.7698 | 14.1 | 7.69 | 17.9843 | Y |  | 5
29 | NF | NF | NF | 0.034 | 0.034 | NF | 0.044 | 2365 | 0.63 | 118.9209 | 74.9202 | 17.3 | 7.69 | 14.4641 | Y |  | 5
30 | 0.03 | 0.04 | 0.04 | 0.02 | 0.02 | 0.03 | 0.06 | 2357 | 0.59 | 119.3246 | 70.4015 | 16.1 | 7.7 | 15.6573 | Y |  | 5
31 | [16 empty] | 5
AVG. | 0.021625 | 0.023714 | 0.02275 | 0.025385 | 0.023296 | 0.022538 | 0.053034 | 2237.4828 | 0.6831 | 128.6428 | 89.1261 | 13.7966 | 7.7448 | 18.8711
MAX. | 0.03 | 0.04 | 0.04 | 0.06 | 0.034 | 0.032 | 0.1 | 2561
MIN | Conventional Filtration | [7 empty] | 0.48
95% of 4 hr turbidity readings </= 0.3 NTU? Y | [5 empty] | All turbidity readings < IFE2 triggers? Y |  |  |  |  | CT's met everyday? Yes |  |  | All Cl2 Residual at entry point
All the 4 hr turbidity readings </= 1.0 NTU? Y | [13 empty] | >/= 0.2 mg/L Yes
1 Including continuous turbidity data, if applicable, for optimization recording purposes. Compliance values in Columns "12am through 8pm" may not correspond to continuous readings maximum.
2 IFE = Individual Filter Effluent | [7 empty] | Name (Printed): | Jaegar T Howatt |  |  | Signature:
3 If Cl2 at entry point <0.2 mg/l, or CT not met, notify DWP by end of next business day. | [7 empty] | Operator Cert. #: | T-448091 |  |  | Date: | 2025-05-04
4 NF=No Flow | [7 empty] | Phone #: | 541-570-7561