## Sheet1
OHA - Drinking Water Program - Turbidity Monitoring Report Form County: Linn Conventional Filtration
Sweet Home, City of |  |  |  | I.D. # OR4100851 |  |  | WTP: WTP-B |  | Month of | 2025-07-01 |  |  |  | Required Log inactivation: |  | 0.5
| TURBIDITY | [5 empty] | Highest | Peak Hourly | Min.Cl2 Res. | CONTACT | ACTUAL | TEMP |  | REQ. | CT | log *
| 12AM | 4AM | 8AM | NOON | 4PM | 8PM | Reading of Day 1 | Demand Flow | at 1st user | TIME | (CT) |  | pH | CT | MET? | inacti-
DATE | NTU | NTU | NTU | NTU | NTU | NTU | (NTU) | (gpm) | Mg/L (C)3 | MIN. (T) | C X T | Co |  | Formula | Y / N | vation
1 | NF | NF | NF | 0.03 | 0.03 | 0.03 | 0.1 | 1858 | 0.59 | 151.3714 | 89.3091 | 14.9 | 7.24 | 14.303 | Y |  | 5
2 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.1 | 1831 | 0.67 | 153.6035 | 102.9143 | 15.8 | 7.41 | 14.4769 | Y |  | 5
3 | 0.03 | 0.03 | 0.03 | NF | 0.03 | 0.03 | 0.05 | 1816 | 0.65 | 154.8722 | 100.667 | 13.2 | 7.31 | 16.5549 | Y |  | 5
4 | 0.03 | NF | NF | 0.03 | 0.03 | 0.03 | 0.05 | 1837 | 0.65 | 153.1018 | 99.5162 | 14.2 | 7.42 | 16.1313 | Y |  | 5
5 | 0.03 | 0.03 | NF | 0.03 | 0.03 | NF | 0.05 | 1828 | 0.51 | 153.8556 | 78.4663 | 13.5 | 7.32 | 16.0301 | Y |  | 5
6 | NF | NF | NF | NF | 0.03 | NF | 0.05 | 1808 | 0.68 | 155.5575 | 105.7791 | 13.6 | 7.37 | 16.5378 | Y |  | 5
7 | NF | NF | NF | 0.03 | 0.03 | 0.03 | 0.05 | 1844 | 0.62 | 152.5206 | 94.5628 | 15.4 | 7.37 | 14.5666 | Y |  | 5
8 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | NF | 0.04 | 1829 | 0.67 | 153.7715 | 103.0269 | 13.3 | 7.33 | 16.6049 | Y |  | 5
9 | NF | 0.04 | 0.03 | 0.03 | 0.03 | 0.03 | 0.07 | 1832 | 0.66 | 153.5197 | 101.323 | 13.4 | 7.37 | 16.7214 | Y |  | 5
10 | 0.03 | NF | NF | NF | 0.02 | 0.03 | 0.07 | 1830 | 0.45 | 153.6874 | 69.1593 | 13.8 | 6.74 | 12.5804 | Y |  | 5
11 | 0.04 | 0.03 | 0.03 | 0.02 | 0.03 | 0.03 | 0.06 | 1825 | 0.47 | 154.1085 | 72.431 | 13.3 | 7.42 | 16.7808 | Y |  | 5
12 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.06 | 1820 | 0.39 | 154.5319 | 60.2674 | 13.8 | 7.39 | 15.9064 | Y |  | 5
13 | 0.04 | NF | NF | NF | 0.03 | 0.03 | 0.06 | 1835 | 0.6 | 153.2687 | 91.9612 | 14.8 | 7.38 | 15.1839 | Y |  | 5
14 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04 | 0.07 | 1842 | 0.57 | 152.6862 | 87.0311 | 12.4 | 7.34 | 17.7129 | Y |  | 5
15 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04 | 0.03 | 0.07 | 1834 | 0.48 | 153.3522 | 73.6091 | 13.6 | 7.38 | 16.2257 | Y |  | 5
16 | 0.03 | NF | NF | 0.04 | 0.05 | 0.08 | 0.1 | 1831 | 0.5 | 153.6035 | 76.8017 | 14.8 | 7.56 | 16.047 | Y |  | 5
17 | 0.03 | 0.03 | NF | 0.03 | 0.03 | 0.03 | 0.1 | 1838 | 0.68 | 153.0185 | 104.0526 | 11.9 | 7.59 | 20.1913 | Y |  | 5
18 | 0.03 | 0.1 | 0.03 | 0.03 | 0.03 | 0.03 | 0.1 | 1824 | 0.66 | 154.193 | 101.7674 | 13.4 | 7.33 | 16.4759 | Y |  | 5
19 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.06 | 1826 | 0.66 | 154.0241 | 101.6559 | 12.6 | 7.31 | 17.2491 | Y |  | 5
20 | 0.03 | NF | NF | NF | 0.03 | 0.02 | 0.07 | 1820 | 0.53 | 154.5319 | 81.9019 | 12.3 | 7.29 | 17.4477 | Y |  | 5
21 | 0.06 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.08 | 1830 | 0.65 | 153.6874 | 99.8968 | 12.7 | 7.34 | 17.3061 | Y |  | 5
22 | 0.03 | 0.03 | 0.03 | 0.02 | 0.03 | NF | 0.05 | 1833 | 0.65 | 153.4359 | 99.7333 | 13.8 | 7.25 | 15.5565 | Y |  | 5
23 | NF | 0.03 | 0.03 | 0.03 | NF | 0.13 | 0.34 | 1827 | 0.67 | 153.9398 | 103.1397 | 13.1 | 7.34 | 16.8898 | Y |  | 5
24 | 0.03 | 0.02 | 0.02 | 0.03 | 0.03 | 0.03 | 0.12 | 1822 | 0.73 | 154.3622 | 112.6844 | 13.7 | 7.41 | 16.7679 | Y |  | 5
25 | 0.03 | NF | NF | 0.03 | 0.03 | 0.03 | 0.07 | 1826 | 0.69 | 154.0241 | 106.2766 | 13.8 | 7.32 | 16.0379 | Y |  | 5
26 | 0.03 | NF | 0.03 | 0.03 | NF | NF | 0.07 | 1818 | 0.71 | 154.7019 | 109.8383 | 14.1 | 7.34 | 15.8733 | Y |  | 5
27 | NF | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.11 | 1819 | 0.69 | 154.6168 | 106.6856 | 14.6 | 7.38 | 15.5465 | Y |  | 5
28 | NF | NF | NF | 0.03 | 0.03 | 0.03 | 0.06 | 1831 | 0.68 | 153.6035 | 104.4504 | 13.1 | 7.33 | 16.8466 | Y |  | 5
29 | 0.03 | NF | 0.03 | 0.03 | 0.03 | NF | 0.04 | 1830 | 0.68 | 153.6874 | 104.5075 | 13.1 | 7.37 | 17.0976 | Y |  | 5
30 | NF | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.06 | 1819 | 0.68 | 154.6168 | 105.1394 | 14 | 7.39 | 16.2225 | Y |  | 5
31 | 0.03 | NF | NF | NF | 0.02 | 0.03 | 0.06 | 1849 | 0.68 | 152.1082 | 103.4336 | 13.6 | 7.4 | 16.7223 | Y |  | 5
AVG. | 0.032174 | 0.033889 | 0.029444 | 0.0296 | 0.030345 | 0.0368 | 0.07871 | 1829.4194 | 0.61935 | 153.7408 | 95.2255 | 13.6645 | 7.3465 | 16.2773
MAX. | 0.06 | 0.1 | 0.03 | 0.04 | 0.05 | 0.13 | 0.34 | 1858
MIN | Conventional Filtration | [7 empty] | 0.39
95% of 4 hr turbidity readings </= 0.3 NTU? Y | [5 empty] | All turbidity readings < IFE2 triggers? Y |  |  |  |  | CT's met everyday? Yes |  |  | All Cl2 Residual at entry point
All the 4 hr turbidity readings </= 1.0 NTU? Y | [13 empty] | >/= 0.2 mg/L Yes
1 Including continuous turbidity data, if applicable, for optimization recording purposes. Compliance values in Columns "12am through 8pm" may not correspond to continuous readings maximum.
2 IFE = Individual Filter Effluent | [7 empty] | Name (Printed): | Jaegar T Howatt |  |  | Signature:
3 If Cl2 at entry point <0.2 mg/l, or CT not met, notify DWP by end of next business day. | [7 empty] | Operator Cert. #: | T-448091 |  |  | Date: | 2025-08-03
4 NF=No Flow | [7 empty] | Phone #: | 541-570-7561