## Sheet1
OHA - Drinking Water Program - Turbidity Monitoring Report Form County: Linn Conventional Filtration
Sweet Home, City of |  |  |  | I.D. # OR4100851 |  |  | WTP: WTP-B |  | Month of | 2025-08-01 |  |  |  | Required Log inactivation: |  | 0.5
| TURBIDITY | [5 empty] | Highest | Peak Hourly | Min.Cl2 Res. | CONTACT | ACTUAL | TEMP |  | REQ. | CT | log *
| 12AM | 4AM | 8AM | NOON | 4PM | 8PM | Reading of Day 1 | Demand Flow | at 1st user | TIME | (CT) |  | pH | CT | MET? | inacti-
DATE | NTU | NTU | NTU | NTU | NTU | NTU | (NTU) | (gpm) | Mg/L (C)3 | MIN. (T) | C X T | Co |  | Formula | Y / N | vation
1 | 0.04 | 0.03 | 0.03 | 0.03 | 0.03 | 0.02 | 0.09 | 1823 | 0.77 | 154.2776 | 118.7937 | 13.7 | 7.38 | 16.6585 | Y |  | 5
2 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.08 | 1818 | 0.76 | 154.7019 | 117.5734 | 13.9 | 7.33 | 16.1184 | Y |  | 5
3 | NF | NF | NF | 0.03 | 0.03 | 0.03 | 0.05 | 1822 | 0.78 | 154.3622 | 120.4025 | 14.1 | 7.38 | 16.239 | Y |  | 5
4 | NF | NF | NF | 0.03 | 0.03 | 0.03 | 0.04 | 1823 | 0.77 | 154.2776 | 118.7937 | 14.5 | 7.35 | 15.6192 | Y |  | 5
5 | 0.03 | 0.03 | NF | 0.03 | 0.03 | 0.03 | 0.05 | 1812 | 0.77 | 155.2141 | 119.5149 | 14.1 | 7.34 | 15.9821 | Y |  | 5
6 | 0.03 | NF | NF | 0.03 | 0.03 | 0.06 | 0.09 | 1802 | 0.75 | 156.0755 | 117.0566 | 15 | 7.31 | 14.8504 | Y |  | 5
7 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.06 | 0.09 | 1807 | 0.71 | 155.6436 | 110.507 | 14.2 | 7.18 | 14.86 | Y |  | 5
8 | 0.03 | 0.03 | 0.03 | 0.03 | NF | NF | 0.05 | 1798 | 0.66 | 156.4227 | 103.239 | 13.2 | 7.33 | 16.6968 | Y |  | 5
9 | NF | NF | NF | 0.03 | 0.03 | 0.03 | 0.08 | 1831 | 0.69 | 153.6035 | 105.9864 | 14.4 | 7.23 | 14.9033 | Y |  | 5
10 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.06 | 0.08 | 1831 | 0.67 | 153.6035 | 102.9143 | 19.2 | 7.26 | 10.8964 | Y |  | 5
11 | 0.03 | 0.03 | 0.03 | 0.03 | NF | 0.03 | 0.09 | 1839 | 0.69 | 152.9353 | 105.5254 | 13.4 | 7.35 | 16.6549 | Y |  | 5
12 | 0.02 | 0.03 | 0.03 | 0.04 | 0.03 | 0.03 | 0.08 | 1830 | 0.79 | 153.6874 | 121.4131 | 12.7 | 7.33 | 17.5187 | Y |  | 5
13 | 0.03 | 0.03 | NF | NF | 0.03 | NF | 0.05 | 1826 | 0.79 | 154.0241 | 121.679 | 12.9 | 7.38 | 17.6094 | Y |  | 5
14 | NF | NF | NF | 0.03 | 0.03 | 0.03 | 0.05 | 1829 | 0.77 | 153.7715 | 118.404 | 14.3 | 7.35 | 15.8289 | Y |  | 5
15 | 0.03 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.07 | 1826 | 0.75 | 154.0241 | 115.5181 | 14 | 7.32 | 15.934 | Y |  | 5
16 | 0.03 | 0.03 | NF | 0.03 | 0.03 | 0.03 | 0.08 | 1814 | 0.76 | 155.043 | 117.8327 | 13.8 | 7.33 | 16.2262 | Y |  | 5
17 | 0.03 | 0.03 | NF | 0.03 | 0.03 | 0.06 | 0.08 | 1819 | 0.78 | 154.6168 | 120.6011 | 15.3 | 7.36 | 14.8791 | Y |  | 5
18 | 0.05 | NF | NF | 0.03 | 0.03 | 0.03 | 0.07 | 1821 | 0.72 | 154.447 | 111.2018 | 13.9 | 7.34 | 16.1047 | Y |  | 5
19 | 0.03 | 0.03 | NF | NF | 0.03 | 0.03 | 0.06 | 1816 | 0.76 | 154.8722 | 117.7029 | 13.8 | 7.33 | 16.2262 | Y |  | 5
20 | 0.03 | 0.03 | 0.03 | NF | 0.02 | 0.03 | 0.05 | 1809 | 0.76 | 155.4715 | 118.1584 | 13.7 | 7.22 | 15.6828 | Y |  | 5
21 | 0.03 | 0.03 | 0.03 | NF | 0.03 | 0.03 | 0.08 | 1819 | 0.76 | 154.6168 | 117.5088 | 13.4 | 7.12 | 15.4179 | Y |  | 5
22 | 0.03 | NF | NF | 0.03 | 0.03 | 0.03 | 0.08 | 1835 | 0.78 | 153.2687 | 119.5496 | 13.8 | 7.22 | 15.6141 | Y |  | 5
23 | 0.03 | NF | NF | 0.03 | 0.03 | 0.03 | 0.05 | 1840 | 0.71 | 152.8522 | 108.525 | 13.9 | 7.15 | 14.9929 | Y |  | 5
24 | NF | 0.03 | 0.03 | 0.07 | 0.03 | 0.03 | 0.07 | 1844 | 0.73 | 152.5206 | 111.34 | 13.2 | 7.21 | 16.0994 | Y |  | 5
25 | 0.03 | NF | NF | 0.03 | 0.07 | 0.03 | 0.09 | 1834 | 0.78 | 153.3522 | 119.6147 | 14.3 | 7.16 | 14.7694 | Y |  | 5
26 | 0.02 | 0.03 | NF | 0.03 | 0.03 | NF | 0.06 | 1843 | 0.8 | 152.6034 | 122.0827 | 14 | 7.23 | 15.4996 | Y |  | 5
27 | NF | NF | 0.03 | 0.03 | 0.03 | 0.03 | 0.04 | 1826 | 0.97 | 154.0241 | 149.4034 | 14.4 | 7.24 | 15.4437 | Y |  | 5
28 | 0.03 | NF | NF | 0.03 | 0.03 | 0.03 | 0.04 | 1811 | 1 | 155.2998 | 155.2998 | 14 | 7.14 | 15.3368 | Y |  | 5
29 | 0.03 | NF | 0.03 | 0.03 | 0.03 | 0.03 | 0.04 | 1829 | 1.01 | 153.7715 | 155.3092 | 13.7 | 7.16 | 15.7811 | Y |  | 5
30 | NF | NF | 0.03 | 0.03 | 0.03 | 0.03 | 0.04 | 1836 | 0.97 | 153.1852 | 148.5896 | 13.2 | 7.15 | 16.1818 | Y |  | 5
31 | NF | NF | 0.03 | 0.02 | 0.02 | 0.03 | 0.04 | 1825 | 0.96 | 154.1085 | 147.9442 | 12.5 | 7.17 | 17.0605 | Y |  | 5
AVG. | 0.030435 | 0.031176 | 0.03 | 0.031481 | 0.03069 | 0.033929 | 0.064839 | 1823.8065 | 0.78613 | 154.2154 | 121.2253 | 14.0161 | 7.2694 | 15.7318
MAX. | 0.05 | 0.05 | 0.03 | 0.07 | 0.07 | 0.06 | 0.09 | 1844
MIN | Conventional Filtration | [7 empty] | 0.66
95% of 4 hr turbidity readings </= 0.3 NTU? Y | [5 empty] | All turbidity readings < IFE2 triggers? Y |  |  |  |  | CT's met everyday? Yes |  |  | All Cl2 Residual at entry point
All the 4 hr turbidity readings </= 1.0 NTU? Y | [13 empty] | >/= 0.2 mg/L Yes
1 Including continuous turbidity data, if applicable, for optimization recording purposes. Compliance values in Columns "12am through 8pm" may not correspond to continuous readings maximum.
2 IFE = Individual Filter Effluent | [7 empty] | Name (Printed): | Jaegar T Howatt |  |  | Signature:
3 If Cl2 at entry point <0.2 mg/l, or CT not met, notify DWP by end of next business day. | [7 empty] | Operator Cert. #: | T-448091 |  |  | Date: | 2025-09-03
4 NF=No Flow | [7 empty] | Phone #: | 541-570-7561