## Sheet1
OHA - Drinking Water Program - Turbidity Monitoring Report Form County: Linn Conventional Filtration
Sweet Home, City of |  |  |  | I.D. # OR4100851 |  |  | WTP: WTP-B |  | Month of | 2025-09-01 |  |  |  | Required Log inactivation: |  | 0.5
| TURBIDITY | [5 empty] | Highest | Peak Hourly | Min.Cl2 Res. | CONTACT | ACTUAL | TEMP |  | REQ. | CT | log *
| 12AM | 4AM | 8AM | NOON | 4PM | 8PM | Reading of Day 1 | Demand Flow | at 1st user | TIME | (CT) |  | pH | CT | MET? | inacti-
DATE | NTU | NTU | NTU | NTU | NTU | NTU | (NTU) | (gpm) | Mg/L (C)3 | MIN. (T) | C X T | Co |  | Formula | Y / N | vation
1 | NF | NF | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 1828 | 0.94 | 153.8556 | 144.6242 | 12.1 | 7.2 | 17.9278 | Y |  | 5
2 | NF | NF | 0.03 | 0.03 | 0.03 | 0.03 | 0.04 | 1818 | 0.96 | 154.7019 | 148.5138 | 14.7 | 7.19 | 14.8426 | Y |  | 5
3 | NF | NF | 0.02 | 0.03 | 0.03 | 0.03 | 0.05 | 1834 | 0.93 | 153.3522 | 142.6176 | 13.6 | 7.13 | 15.5687 | Y |  | 5
4 | 0.03 | 0.03 | NF | 0.03 | 0.03 | 0.03 | 0.06 | 1838 | 0.96 | 153.0185 | 146.8978 | 14.2 | 7.17 | 15.233 | Y |  | 5
5 | NF | NF | NF | 0.02 | 0.03 | 0.03 | 0.08 | 1827 | 0.92 | 153.9398 | 141.6246 | 14.5 | 7.21 | 15.0852 | Y |  | 5
6 | 0.03 | 0.03 | NF | 0.03 | 0.03 | 0.03 | 0.08 | 1833 | 0.88 | 153.4359 | 135.0236 | 14.4 | 7.14 | 14.7297 | Y |  | 5
7 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04 | 0.03 | 0.06 | 1822 | 0.88 | 154.3622 | 135.8388 | 14.2 | 7.14 | 14.9278 | Y |  | 5
8 | 0.03 | 0.03 | 0.03 | 0.03 | NF | NF | 0.04 | 1834 | 0.95 | 153.3522 | 145.6846 | 14.7 | 7.14 | 14.5532 | Y |  | 5
9 | NF | NF | 0.03 | 0.03 | 0.03 | 0.03 | 0.04 | 1825 | 0.87 | 154.1085 | 134.0744 | 14.3 | 7.19 | 15.0887 | Y |  | 5
10 | NF | NF | NF | 0.02 | 0.03 | 0.03 | 0.05 | 1825 | 0.9 | 154.1085 | 138.6976 | 14 | 7.21 | 15.5615 | Y |  | 5
11 | 0.03 | NF | NF | NF | 0.03 | 0.03 | 0.05 | 1817 | 0.91 | 154.787 | 140.8562 | 13.4 | 7.05 | 15.2821 | Y |  | 5
12 | 0.03 | 0.03 | NF | 0.03 | 0.03 | 0.03 | 0.04 | 1811 | 0.9 | 155.2998 | 139.7699 | 13.6 | 7.15 | 15.6309 | Y |  | 5
13 | 0.03 | NF | NF | 0.03 | 0.03 | 0.03 | 0.04 | 1830 | 0.9 | 153.6874 | 138.3187 | 14.5 | 7.16 | 14.7743 | Y |  | 5
14 | NF | NF | NF | 0.03 | 0.03 | 0.03 | 0.05 | 1823 | 0.85 | 154.2776 | 131.1359 | 15.1 | 7.19 | 14.2709 | Y |  | 5
15 | 0.03 | NF | NF | NF | NF | 0.03 | 0.05 | 1815 | 0.87 | 154.9576 | 134.8131 | 15.1 | 7.15 | 14.0926 | Y |  | 5
16 | 0.03 | 0.03 | 0.03 | 0.03 | NF | NF | 0.06 | 1831 | 0.85 | 153.6035 | 130.563 | 14.2 | 7.05 | 14.3882 | Y |  | 5
17 | NF | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.09 | 1835 | 0.76 | 153.2687 | 116.4842 | 14.5 | 7.2 | 14.7576 | Y |  | 5
18 | 0.03 | NF | NF | NF | 0.03 | 0.03 | 0.05 | 1829 | 0.76 | 153.7715 | 116.8663 | 14.2 | 7.14 | 14.7249 | Y |  | 5
19 | 0.03 | NF | NF | 0.03 | 0.03 | NF | 0.04 | 1818 | 0.85 | 154.7019 | 131.4966 | 14.2 | 7.2 | 15.2115 | Y |  | 5
20 | NF | NF | NF | 0.03 | 0.03 | 0.03 | 0.05 | 1839 | 0.8 | 152.9353 | 122.3482 | 14.6 | 7.19 | 14.6718 | Y |  | 5
21 | 0.03 | 0.03 | 0.03 | NF | 0.03 | 0.03 | 0.05 | 1816 | 0.85 | 154.8722 | 131.6414 | 14.3 | 7.16 | 14.8878 | Y |  | 5
22 | NF | NF | NF | 0.03 | 0.03 | 0.03 | 0.06 | 1826 | 0.77 | 154.0241 | 118.5986 | 14.9 | 7.13 | 14.0156 | Y |  | 5
23 | 0.03 | NF | NF | NF | 0.02 | 0.03 | 0.05 | 1829 | 0.83 | 153.7715 | 127.6303 | 15.7 | 7.27 | 14.0908 | Y |  | 5
24 | 0.03 | 0.03 | NF | NF | 0.03 | 0.03 | 0.05 | 1823 | 0.87 | 154.2776 | 134.2215 | 16.6 | 7.2 | 12.9851 | Y |  | 5
25 | NF | NF | 0.03 | NF | 0.03 | 0.03 | 0.07 | 1826 | 0.81 | 154.0241 | 124.7595 | 14.9 | 7.15 | 14.1848 | Y |  | 5
26 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04 | 0.09 | 1824 | 0.83 | 154.193 | 127.9802 | 15.8 | 7.25 | 13.8933 | Y |  | 5
27 | 0.03 | 0.03 | NF | NF | 0.04 | 0.03 | 0.05 | 1809 | 0.74 | 155.4715 | 115.0489 | 15.6 | 7.23 | 13.8332 | Y |  | 5
28 | 0.03 | 0.03 | NF | NF | 0.03 | 0.03 | 0.05 | 1815 | 0.84 | 154.9576 | 130.1644 | 17.2 | 7.27 | 12.7585 | Y |  | 5
29 | 0.03 | 0.03 | NF | NF | 0.03 | 0.03 | 0.08 | 1808 | 0.88 | 155.5575 | 136.8906 | 16 | 7.27 | 13.89 | Y |  | 5
30 | NF | NF | NF | 0.03 | 0.03 | NF | 0.05 | 1820 | 0.86 | 154.5319 | 132.8974 | 15.4 | 7.29 | 14.5331 | Y |  | 5
31 | [9 empty] | #DIV/0! | #DIV/0! |  |  | 4.185 | #DIV/0! |  | 5
AVG. | 0.03 | 0.03 | 0.029091 | 0.029 | 0.03037 | 0.030385 | 0.055667 | 1824.2667 | 0.864 | #DIV/0! | #DIV/0! | 14.6833 | 7.1807 | 14.3413
MAX. | 0.03 | 0.03 | 0.03 | 0.03 | 0.04 | 0.04 | 0.09 | 1839
MIN | Conventional Filtration | [7 empty] | 0.74
95% of 4 hr turbidity readings </= 0.3 NTU? Y | [5 empty] | All turbidity readings < IFE2 triggers? Y |  |  |  |  | CT's met everyday? Yes |  |  | All Cl2 Residual at entry point
All the 4 hr turbidity readings </= 1.0 NTU? Y | [13 empty] | >/= 0.2 mg/L Yes
1 Including continuous turbidity data, if applicable, for optimization recording purposes. Compliance values in Columns "12am through 8pm" may not correspond to continuous readings maximum.
2 IFE = Individual Filter Effluent | [7 empty] | Name (Printed): | Jaegar T Howatt |  |  | Signature:
3 If Cl2 at entry point <0.2 mg/l, or CT not met, notify DWP by end of next business day. | [7 empty] | Operator Cert. #: | T-448091 |  |  | Date: | 2025-10-02
4 NF=No Flow | [7 empty] | Phone #: | 541-570-7561