## Sheet1
OHA - Drinking Water Program - Turbidity Monitoring Report Form County: Linn Conventional Filtration
Sweet Home, City of |  |  |  | I.D. # OR4100851 |  |  | WTP: WTP-B |  | Month of | 2025-10-01 |  |  |  | Required Log inactivation: |  | 0.5
| TURBIDITY | [5 empty] | Highest | Peak Hourly | Min.Cl2 Res. | CONTACT | ACTUAL | TEMP |  | REQ. | CT | log *
| 12AM | 4AM | 8AM | NOON | 4PM | 8PM | Reading of Day 1 | Demand Flow | at 1st user | TIME | (CT) |  | pH | CT | MET? | inacti-
DATE | NTU | NTU | NTU | NTU | NTU | NTU | (NTU) | (gpm) | Mg/L (C)3 | MIN. (T) | C X T | Co |  | Formula | Y / N | vation
1 | NF | NF | 0.03 | 0.03 | 0.03 | NF | 0.06 | 1825 | 0.81 | 154.1085 | 124.8279 | 16.2 | 7.41 | 14.322 | Y |  | 5
2 | 0.03 | 0.03 | NF | NF | 0.03 | 0.02 | 0.04 | 1811 | 0.89 | 155.2998 | 138.2169 | 16.3 | 7.39 | 14.2509 | Y |  | 5
3 | 0.03 | NF | NF | NF | 0.03 | 0.03 | 0.05 | 1807 | 0.94 | 155.6436 | 146.305 | 15.1 | 7.29 | 14.9632 | Y |  | 5
4 | 0.03 | NF | NF | NF | 0.02 | 0.02 | 0.06 | 1814 | 0.93 | 155.043 | 144.19 | 15.6 | 7.28 | 14.4016 | Y |  | 5
5 | 0.02 | NF | NF | NF | NF | 0.02 | 0.04 | 1783 | 0.97 | 157.7386 | 153.0065 | 14.8 | 7.19 | 14.7606 | Y |  | 5
6 | 0.02 | 0.02 | NF | NF | 0.02 | 0.02 | 0.05 | 1809 | 0.94 | 155.4715 | 146.1432 | 16.7 | 7.4 | 14.0061 | Y |  | 5
7 | NF | NF | NF | 0.02 | 0.02 | 0.02 | 0.06 | 1806 | 0.88 | 155.7298 | 137.0422 | 16.6 | 7.52 | 14.6419 | Y |  | 5
8 | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF |  | 5
9 | NF | NF | 0.02 | 0.02 | 0.02 | 0.02 | 0.07 | 1819 | 0.91 | 154.6168 | 140.7013 | 14.9 | 7.29 | 15.1126 | Y |  | 5
10 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | NF | 0.03 | 1808 | 0.96 | 155.5575 | 149.3352 | 14.8 | 7.41 | 15.9962 | Y |  | 5
11 | NF | NF | NF | NF | 0.02 | 0.02 | 0.04 | 1714 | 0.89 | 164.0887 | 146.0389 | 15 | 7.4 | 15.6011 | Y |  | 5
12 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03 | NF | 0.03 | 1576 | 0.89 | 178.4569 | 158.8266 | 14.8 | 7.33 | 15.4059 | Y |  | 5
13 | NF | NF | NF | 0.03 | 0.03 | 0.03 | 0.04 | 1576 | 0.91 | 178.4569 | 162.3957 | 15.3 | 7.28 | 14.6598 | Y |  | 5
14 | 0.03 | 0.03 | NF | 0.03 | 0.03 | 0.03 | 0.03 | 1572 | 0.94 | 178.9109 | 168.1763 | 16.8 | 7.64 | 15.2088 | Y |  | 5
15 | NF | NF | 0.03 | 0.03 | 0.02 | NF | 0.04 | 1584 | 0.96 | 177.5556 | 170.4533 | 15.2 | 7.51 | 16.1627 | Y |  | 5
16 | NF | NF | 0.03 | 0.03 | 0.03 | 0.03 | 0.06 | 1572 | 0.94 | 178.9109 | 168.1763 | 15.1 | 7.49 | 16.1141 | Y |  | 5
17 | 0.03 | NF | NF | NF | 0.03 | 0.03 | 0.06 | 1564 | 1.03 | 179.8261 | 185.2209 | 16.1 | 7.58 | 15.7462 | Y |  | 5
18 | 0.03 | NF | NF | 0.03 | 0.03 | 0.02 | 0.06 | 1566 | 0.96 | 179.5964 | 172.4126 | 15.6 | 7.54 | 15.9133 | Y |  | 5
19 | 0.03 | NF | NF | NF | 0.03 | 0.03 | 0.05 | 1567 | 0.93 | 179.4818 | 166.9181 | 16.2 | 7.57 | 15.4072 | Y |  | 5
20 | 0.03 | NF | NF | 0.03 | 0.03 | NF | 0.05 | 1573 | 0.91 | 178.7972 | 162.7055 | 17 | 7.49 | 14.146 | Y |  | 5
21 | NF | NF | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 1572 | 0.92 | 178.9109 | 164.5981 | 16.1 | 7.51 | 15.1519 | Y |  | 5
22 | 0.02 | NF | 0.08 | 0.03 | 0.03 | 0.03 | 0.08 | 1568 | 0.93 | 179.3673 | 166.8116 | 17.2 | 7.63 | 14.7364 | Y |  | 5
23 | 0.03 | NF | NF | 0.03 | 0.03 | 0.03 | 0.06 | 1561 | 0.93 | 180.1717 | 167.5597 | 16.3 | 7.58 | 15.3615 | Y |  | 5
24 | NF | NF | NF | 0.04 | 0.03 | 0.03 | 0.07 | 1566 | 0.87 | 179.5964 | 156.2489 | 15.8 | 7.57 | 15.716 | Y |  | 5
25 | 0.03 | 0.03 | NF | NF | 0.03 | 0.03 | 0.04 | 1564 | 0.86 | 179.8261 | 154.6504 | 15.9 | 7.59 | 15.7097 | Y |  | 5
26 | NF | NF | NF | 0.03 | 0.03 | 0.03 | 0.06 | 1572 | 0.81 | 178.9109 | 144.9179 | 15.8 | 7.48 | 15.0969 | Y |  | 5
27 | 0.03 | NF | NF | 0.04 | 0.03 | 0.03 | 0.07 | 1568 | 0.81 | 179.3673 | 145.2876 | 15.4 | 7.52 | 15.7368 | Y |  | 5
28 | 0.03 | NF | NF | NF | 0.03 | 0.03 | 0.07 | 1559 | 0.83 | 180.4028 | 149.7343 | 17.1 | 7.62 | 14.6125 | Y |  | 5
29 | 0.03 | 0.04 | NF | 0.03 | 0.04 | 0.03 | 0.06 | 1550 | 0.83 | 181.4503 | 150.6038 | 16.5 | 7.48 | 14.4402 | Y |  | 5
30 | NF | NF | NF | NF | 0.03 | 0.03 | 0.06 | 1569 | 0.75 | 179.253 | 134.4398 | 16.2 | 7.51 | 14.7621 | Y |  | 5
31 | 0.03 | NF | NF | 0.04 | 0.03 | 0.03 | 0.07 | 1554 | 0.69 | 180.9833 | 124.8785 | 18 | 7.54 | 13.1435 | Y |  | 5
AVG. | 0.027368 | 0.027143 | 0.0325 | 0.029474 | 0.027931 | 0.0268 | 0.053667 | 1644.9667 | 0.894 | 171.7177 | 153.3608 | 15.9467 | 7.468 | 15.0429
MAX. | 0.03 | 0.04 | 0.08 | 0.04 | 0.04 | 0.03 | 0.08 | 1825
MIN | Conventional Filtration | [7 empty] | 0.69
95% of 4 hr turbidity readings </= 0.3 NTU? Y | [5 empty] | All turbidity readings < IFE2 triggers? Y |  |  |  |  | CT's met everyday? Yes |  |  | All Cl2 Residual at entry point
All the 4 hr turbidity readings </= 1.0 NTU? Y | [13 empty] | >/= 0.2 mg/L Yes
1 Including continuous turbidity data, if applicable, for optimization recording purposes. Compliance values in Columns "12am through 8pm" may not correspond to continuous readings maximum.
2 IFE = Individual Filter Effluent | [7 empty] | Name (Printed): | Jaegar T Howatt |  |  | Signature:
3 If Cl2 at entry point <0.2 mg/l, or CT not met, notify DWP by end of next business day. | [7 empty] | Operator Cert. #: | T-448091 |  |  | Date: | 2025-11-03
4 NF=No Flow | [7 empty] | Phone #: | 541-570-7561