## Sheet1
OHA - Drinking Water Program - Turbidity Monitoring Report Form County: Linn Conventional Filtration
Sweet Home, City of |  |  |  | I.D. # OR4100851 |  |  | WTP: WTP-B |  | Month of | 2025-11-01 |  |  |  | Required Log inactivation: |  | 0.5
| TURBIDITY | [5 empty] | Highest | Peak Hourly | Min.Cl2 Res. | CONTACT | ACTUAL | TEMP |  | REQ. | CT | log *
| 12AM | 4AM | 8AM | NOON | 4PM | 8PM | Reading of Day 1 | Demand Flow | at 1st user | TIME | (CT) |  | pH | CT | MET? | inacti-
DATE | NTU | NTU | NTU | NTU | NTU | NTU | (NTU) | (gpm) | Mg/L (C)3 | MIN. (T) | C X T | Co |  | Formula | Y / N | vation
1 | NF | NF | NF | 0.03 | 0.03 | 0.03 | 0.07 | 1566 | 0.76 | 179.5964 | 136.4933 | 15.6 | 7.5 | 15.3261 | Y |  | 5
2 | NF | NF | NF | 0.04 | 0.03 | 0.03 | 0.08 | 1521 | 0.8 | 184.9099 | 147.9279 | 15.1 | 7.48 | 15.8007 | Y |  | 5
3 | 0.03 | 0.03 | NF | 0.04 | NF | 0.02 | 0.05 | 1809 | 0.8 | 155.4715 | 124.3772 | 15.6 | 7.52 | 15.5106 | Y |  | 5
4 | 0.03 | NF | 0.03 | 0.02 | NF | NF | 0.06 | 1521 | 0.78 | 184.9099 | 144.2297 | 15.3 | 7.55 | 15.9644 | Y |  | 5
5 | NF | NF | 0.03 | 0.03 | 0.03 | 0.03 | 0.06 | 1808 | 0.74 | 155.5575 | 115.1126 | 16.7 | 7.5 | 14.2079 | Y |  | 5
6 | 0.04 | 0.04 | 0.04 | NF | 0.04 | 0.03 | 0.08 | 1784 | 0.63 | 157.6502 | 99.3196 | 15.9 | 7.52 | 14.9114 | Y |  | 5
7 | 0.03 | NF | NF | NF | 0.03 | 0.03 | 0.06 | 1521 | 0.74 | 184.9099 | 136.8333 | 15.3 | 7.32 | 14.5932 | Y |  | 5
8 | 0.03 | 0.03 | NF | NF | NF | 0.03 | 0.05 | 1508 | 0.78 | 186.504 | 145.4731 | 14.8 | 7.45 | 15.9056 | Y |  | 5
9 | 0.03 | 0.03 | NF | NF | 0.03 | 0.05 | 0.06 | 1517 | 0.74 | 185.3975 | 137.1941 | 14.5 | 7.4 | 15.8569 | Y |  | 5
10 | .03. | NF | NF | 0.03 | 0.03 | NF | 0.07 | 1507 | 0.77 | 186.6277 | 143.7034 | 16 | 7.43 | 14.5563 | Y |  | 5
11 | NF | NF | NF | 0.02 | 0.03 | 0.03 | 0.06 | 1505 | 0.74 | 186.8757 | 138.2881 | 16.1 | 7.35 | 13.9881 | Y |  | 5
12 | 0.03 | NF | NF | 0.03 | NF | 0.03 | 0.07 | 1513 | 0.77 | 185.8876 | 143.1335 | 16.4 | 7.41 | 14.0674 | Y |  | 5
13 | 0.03 | 0.02 | NF | 0.03 | 0.03 | 0.02 | 0.1 | 1475 | 0.57 | 190.6766 | 108.6857 | 15.4 | 7.47 | 15.0312 | Y |  | 5
14 | 0.03 | NF | NF | 0.03 | 0.03 | 0.02 | 0.04 | 1509 | 0.77 | 186.3804 | 143.5129 | 14.7 | 7.44 | 15.9347 | Y |  | 5
15 | 0.02 | NF | NF | 0.02 | 0.02 | 0.02 | 0.04 | 1520 | 0.79 | 185.0316 | 146.1749 | 15.7 | 7.53 | 15.4471 | Y |  | 5
16 | NF | NF | 0.04 | 0.03 | 0.02 | 0.03 | 0.05 | 1521 | 0.79 | 184.9099 | 146.0788 | 15 | 7.53 | 16.1851 | Y |  | 5
17 | 0.02 | NF | NF | 0.03 | 0.03 | 0.02 | 0.07 | 1515 | 0.78 | 185.6422 | 144.801 | 15.6 | 7.53 | 15.5327 | Y |  | 5
18 | NF | NF | NF | 0.02 | 0.03 | 0.02 | 0.05 | 1511 | 0.7 | 186.1337 | 130.2936 | 15 | 7.46 | 15.6102 | Y |  | 5
19 | 0.02 | NF | NF | NF | 0.03 | 0.02 | 0.04 | 1357 | 0.75 | 207.2572 | 155.4429 | 14.4 | 7.54 | 16.8307 | Y |  | 5
20 | 0.02 | 0.02 | 0.03 | NF | 0.02 | NF | 0.03 | 1505 | 0.79 | 186.8757 | 147.6318 | 14.3 | 7.51 | 16.8326 | Y |  | 5
21 | NF | NF | NF | 0.03 | 0.03 | 0.03 | 0.04 | 1519 | 0.72 | 185.1534 | 133.3104 | 14.3 | 7.48 | 16.5149 | Y |  | 5
22 | 0.02 | NF | NF | NF | 0.03 | 0.03 | 0.08 | 1509 | 0.72 | 186.3804 | 134.1939 | 13.8 | 7.47 | 17.011 | Y |  | 5
23 | NF | NF | NF | 0.03 | 0.03 | 0.03 | 0.05 | 1515 | 0.74 | 185.6422 | 137.3753 | 13.6 | 7.43 | 17.0246 | Y |  | 5
24 | NF | NF | NF | 0.03 | 0.09 | 0.08 | 0.09 | 1512 | 0.74 | 186.0106 | 137.6478 | 15.1 | 7.5 | 15.8098 | Y |  | 5
25 | NF | NF | 0.03 | 0.02 | 0.03 | 0.03 | 0.09* | 1510 | 0.79 | 186.257 | 147.143 | 16.7 | 7.48 | 14.1835 | Y |  | 5
26 | 0.03 | 0.04 | NF | 0.02 | 0.02 | 0.04 | 0.04 | 1511 | 0.81 | 186.1337 | 150.7683 | 13.3 | 7.44 | 17.5713 | Y |  | 5
27 | 0.03 | NF | NF | 0.04 | 0.03 | 0.03 | 0.09 | 1495 | 0.8 | 188.1258 | 150.5006 | 13.1 | 7.46 | 17.9182 | Y |  | 5
28 | 0.03 | NF | NF | NF | 0.02 | 0.03 | 0.07 | 1520 | 0.74 | 185.0316 | 136.9234 | 13.1 | 7.43 | 17.6004 | Y |  | 5
29 | 0.03 | 0.03 | NF | NF | 0.03 | 0.03 | 0.04 | 1513 | 0.74 | 185.8876 | 137.5569 | 13.5 | 7.43 | 17.1382 | Y |  | 5
30 | 0.03 | 0.03 | NF | NF | 0.03 | 0.03 | 0.06 | 1497 | 0.54 | 187.8744 | 101.4522 | 12.1 | 7.36 | 18.1225 | Y |  | 5
DATE: 31 |  | #DIV/0! | #DIV/0! |  |  | 4.185 | #DIV/0! |  | 5
AVG. | 0.027895 | 0.03 | 0.033333 | 0.0285 | 0.030769 | 0.03037 | 0.060345 | 1536.4667 | 0.74433 | #DIV/0! | #DIV/0! | 14.8667 | 7.464 | 15.5217
MAX. | 0.04 | 0.04 | 0.04 | 0.04 | 0.09 | 0.08 | 0.1 | 1809
DATE: MIN; NTU: Conventional Filtration | 0.54
DATE: 95% of 4 hr turbidity readings </= 0.3 NTU? Y; NTU: All turbidity readings < IFE2 triggers? Y |  |  | CT's met everyday? Yes |  |  | All Cl2 Residual at entry point
DATE: All the 4 hr turbidity readings </= 1.0 NTU? Y | [5 empty] | >/= 0.2 mg/L Yes
1 Including continuous turbidity data, if applicable, for optimization recording purposes. Compliance values in Columns "12am through 8pm" may not correspond to continuous readings maximum.
DATE: 2 IFE = Individual Filter Effluent; (gpm): Name (Printed): | Jaegar T Howatt |  |  | Signature:
DATE: 3 If Cl2 at entry point <0.2 mg/l, or CT not met, notify DWP by end of next business day.; (gpm): Operator Cert. #: | T-448091 |  |  | Date: | 2025-12-01
DATE: 4 NF=No Flow; (gpm): Phone #: | 541-570-7561
*A highest recorded reading of 0.68 on this day was not actual and replaced with next highest reading. While working with programmer
a misinput caused the filter to go "effluent to clearwell" before the turbidimeter had a chance to "clean up". The water being filtered at the time was 0.03.
JH